## Overview_data
GOLD_E_F_BACnet_230307
BACnet IP
GOLD RX/PX/CX/SD, GENERATION E/F
Applicable to program version 1.10 and newer versions
Overview
This BACnet driver is implemented in GOLD PV 2.40 and provides the function
of monitoring and operating the air handling unit.
GOLD is a BACnet Advanced Application Controller (B-AAC).
The supported Data Link Layer Options are BACnet / IP.
See also document BACnet PICS (Protocol Implementation Conformance Statement) GOLD
and GOLD EDE (Engineering Data Exchange).
BACnet Interoperability Building Blocks Supported.
Data Sharing |  | DS-RP-B | Data Sharing-Read Property-B
|  | DS-RPM-B | Data Sharing-Read Property Multiple-B
|  | DS-WP-B | Data Sharing-Write Property-B
|  | DS-WPM-B | Data Sharing-Write Property Multiple-B
|  | DS-COV-B | Data Sharing-COV-B
|  | DS-COVP-B | Data Sharing-COV Property-B
Alarm&Event Management |  | AE-N-I-B | Alarm&Event-Notification Internal-B
|  | AE-ACK-B | Alarm&Event-Acknowledge Alarm-B
|  | AE-INFO-B | Alarm&Event-Event Information-B
|  | AE-ASUM-B | Alarm&Event-Alarm Summary-B
|  | AE-ESUM-B | Alarm&Event-Enrollment Summary -B
Scheduling |  | SCHED-I-B | Scheduling-Internal-B
Device Management |  | DM-DDB-A | Device Management-Dynamic Device Binding-A
|  | DM-DDB-B | Device Management-Dynamic Device Binding-B
|  | DM-DOB-B | Device Management-Dynamic Object Binding-B
|  | DM-DCC-B | Device Management-Dynamic Communication Control-B
|  | DM-TS-B | Device Management-TimeSynchronization-B
|  | DM-UTC-B | Device Management-UTCTimeSynchronization-B
|  | DM-RD-B | Device Management-Reinitialize Device-B
|  | DM-R-B | Device Management-Restart-B
|  | DM-LM-B | Device Management-List Manipulation-B
Standard Object Types Supported.
Object Type | Properties
Device | Object_Identifier, Object_Name, Object_Type, System_Status, Vendor_Name, Vendor_Identifier, Model_Name, Firmware_Revision, Application_Software_Version, Location, Description, Protocol_Version, Protocol_Revision, Protocol_Services_Supported, Protocol_Object_Types_Supported, Object_List, Max_APDU_Length_Accepted, Segmentation_Supported, Max_Segments_Accepted, Local_Time, Local_Date, UTC_Offset, Daylight_Savings_Status, APDU_Segment_Timeout, APDU_Timeout, Number_Of_APDU_Retries, Device_Address_Binding, Database_Revision, Active_COV_Subscriptions, Last_Restart_Reason, Time_Of_Device_Restart, Restart_Notification_Recipients, Property_List1.
Analog Input | Object_Identifier, Object_Name, Object_Type, Present_Value, Description, Status_Flags, Event_State, Reliability, Out_Of_Service, Units, Min_Pres_Value, Max_Pres_Value, Resolution, COV_Increment, Time_Delay, Notification_Class, High_Limit, Low_Limit, Deadband, Limit_Enable, Event_Enable, Acked_Transitions, Notify_Type, Event_Time_Stamps, Event_Detection_Enable1, Property_List1.
Analog Output | Object_Identifier, Object_Name, Object_Type, Present_Value, Description, Status_Flags, Event_State, Reliability, Out_Of_Service, Units, Min_Pres_Value, Max_Pres_Value, Resolution, Priority_Array, Relinquish_Default, COV_Increment, Time_Delay, Notification_Class, High_Limit, Low_Limit, Deadband, Limit_Enable, Event_Enable, Acked_Transitions, Notify_Type, Event_Time_Stamps, Event_Detection_Enable1, Property_List1.
Analog Value | Object_Identifier, Object_Name, Object_Type, Present_Value, Description, Status_Flags, Event_State, Reliability, Out_Of_Service, Units, Priority_Array, Relinquish_Default, COV_Increment, Time_Delay, Notification_Class, High_Limit, Low_Limit, Deadband, Limit_Enable, Event_Enable, Acked_Transitions, Notify_Type, Event_Time_Stamps, Event_Detection_Enable1, Min_Pres_Value1, Max_Pres_Value1, Resolution1, Property_List1.
Binary Input | Object_Identifier, Object_Name, Object_Type, Present_Value, Description, Status_Flags, Event_State, Reliability, Out_Of_Service, Polarity, Time_Delay, Notification_Class, Alarm_Value, Event_Enable, Acked_Transitions, Notify_Type, Event_Time_Stamps, Event_Detection_Enable1, Property_List1.
Binary Output | Object_Identifier, Object_Name, Object_Type, Present_Value, Description, Status_Flags, Event_State, Reliability, Out_Of_Service, Polarity,Priority_Array, Relinquish_Default, Time_Delay, Notification_Class, Feedback_Value, Event_Enable, Acked_Transitions, Notify_Type, Event_Time_Stamps, Event_Detection_Enable1, Property_List1.
Binary Value | Object_Identifier, Object_Name, Object_Type, Present_Value, Description, Status_Flags, Event_State, Reliability, Out_Of_Service, Priority_Array, Relinquish_Default, Time_Delay, Notification_Class, Alarm_Value, Event_Enable, Acked_Transitions, Notify_Type, Event_Time_Stamps, Event_Detection_Enable1, Property_List1.
Calendar | Object_Identifier, Object_Name, Object_Type, Description, Present_Value, Date_List, Property_List1.
Multistate Input | Object_Identifier, Object_Name, Object_Type, Present_Value, Description, Status_Flags, Event_State, Reliability, Out_Of_Service, Number_Of_States, State_Text, Time_Delay, Notification_Class, Alarm_Values, Fault_Values, Event_Enable, Acked_Transitions, Notify_Type, Event_Time_Stamps, Event_Detection_Enable1, Property_List1.
Multistate Output | Object_Identifier, Object_Name, Object_Type, Present_Value, Description, Status_Flags, Event_State, Reliability, Out_Of_Service, Number_Of_States, State_Text, Priority_Array, Relinquish_Default, Time_Delay, Notification_Class, Feedback_Value, Event_Enable, Acked_Transitions, Notify_Type, Event_Time_Stamps, Event_Detection_Enable1, Property_List1.
Multistate Value | Object_Identifier, Object_Name, Object_Type, Present_Value, Description, Status_Flags, Event_State, Reliability, Out_Of_Service, Number_Of_States, State_Text, Priority_Array, Relinquish_Default, Time_Delay, Notification_Class, Alarm_Values, Fault_Values, Event_Enable, Acked_Transitions, Notify_Type, Event_Time_Stamps, Event_Detection_Enable1, Property_List1.
Notification Class | Object_Identifier, Object_Name, Object_Type, Description, Notification_Class, Priority, Ack_Required, Recipient_List, Property_List1.
Schedule | Object_Identifier, Object_Name, Object_Type, Present_Value, Description, Effective_Period, Weekly_Schedule, Exception_Schedule, Schedule_Default, List_Of_Object_Property_References, Priority_For_Writing, Status_Flags, Reliability, Out_Of_Service, Property_List1.
1 New property added from GOLD PV 1.31.

## Overview parameters
GOLD_E_F_BACnet_230307
Operation level |  | MI 592 |  | EA AHU filter pressure level |  | AI 29 |  | EA Temperature |  | AI 66
Communication operation level |  | MV 793 |  | EA AHU filter pressure alarm limit. |  | AI 30 |  | EA/Room temperature set point |  | AV 135
Operation active |  | BI 1 | [5 empty] | SA min temp set point |  | AV 136
Low speed operation active |  | BI 3 | [5 empty] | SA max temp set point |  | AV 137
High speed operation active |  | BI 4 |  |  | EA Duct pressure |  | AI 10
Damper operation active |  | BI 2 |  |  | EA low speed pressure set point |  | AV 20
Triggered alarm #1 |  | AI 604 |  |  | EA high speed pressure set point |  | AV 22 | SA Duct pressure |  | AI 8
A-alarm active |  | BI 13 | [5 empty] | SA low speed pressure set point |  | AV 19
B-alarm active |  | BI 14 | [5 empty] | SA high speed pressure set point |  | AV 21
Alarm reset |  | BV 1
[8 empty] | SA Temperature |  | AI 64
[8 empty] | SA temperature set point |  | AV 132
EA Air flow |  | AI 6 | [5 empty] | ERS 1 diff |  | AV 118
EA Fan level |  | AI 38
EA low speed air flow set point |  | AV 4
EA high speed air flow set point |  | AV 6
Outdoor temperature |  | AI 73
SA AHU filter pressure level |  | AI 27
SA AHU filter pressure alarm limit. |  | AI 28
Heat exchanger regulator level |  | AI 91
RHX operation level |  | AI105
| SA Air flow |  | AI 4 |  | Reheat regulator level |  | AI 94 | Cool regulator level |  | AI 101
| SA Fan level |  | AI 37 |  | Re-heat output |  | BI 38 | Cool output 1 |  | BI 43
| SA low speed air flow set point |  | AV 3 |  | Re-heat anti frost temp/overheat input |  | AI 153 | Cool output 2 |  | BI 44
| SA high speed air flow set point |  | AV 5

## Analog Input
GOLD_E_F_BACnet_230307
Analog Input (RO).
Object Instance | Object Name | Description | Min | Max | Unit | Default | Misc
AHU Air flow/duct pressure
1 | Component name | 25=IQlogic | 0 | 999
Air flow regulation
4 | SA Air flow | Present supply air flow. | 0 | 20000 | l/s
5 | SA Air flow regulator | Present supply air flow regulator set point. | 0 | 20000 | l/s
6 | EA Air flow | Present extract air flow. | 0 | 20000 | l/s
7 | EA Air flow regulator | Present extract air flow regulator set point. | 0 | 20000 | l/s
Pressure regulation
8 | SA Duct pressure | Present supply air duct pressure. | 0.0 | 2000.0 | Pa
9 | SA Duct pressure regulator | Present supply air duct pressure regulator set point. | 0.0 | 2000.0 | Pa
10 | EA Duct pressure | Present extract air duct pressure. | 0.0 | 2000.0 | Pa
11 | EA Duct pressure regulator | Present extract air duct pressure regulator set point. | 0.0 | 2000.0 | Pa
Demand regulation
12 | Demand input level | Present input signal for demand regulation. | 0.00 | 100.00 | %
13 | Demand regulator | Present demand regulator set point. | 0.00 | 100.00 | %
Air flow pressure sensors
14 | SA Air flow pressure | Present air flow pressure in the supply air fan inlet. | 0.0 | 2000.0 | Pa
15 | EA Air flow pressure | Present air flow pressure in the extract air fan inlet. | 0.0 | 2000.0 | Pa
Demand regulation
18 | Demand CO2 regulator | Present demand CO2 regulator set point. | 0 | 10000 | ppm |  | 1.23
19 | Demand VOC regulator | Present demand VOC regulator set point. | 0 | 10000 | ppm |  | 1.23
Filters
23 | SA Pre-filter pressure level | Present supply air pre-filter pressure drop. | 0.0 | 2000.0 | Pa
24 | SA Pre-filter pressure alarm limit | Present supply air pre-filter pressure alarm limit. | 0.0 | 2000.0 | Pa
25 | EA Pre-filter pressure level | Present extract air pre-filter pressure drop. | 0.0 | 2000.0 | Pa
26 | EA Pre-filter pressure alarm limit | Present extract air pre-filter pressure alarm limit. | 0.0 | 2000.0 | Pa
27 | SA AHU filter pressure level | Present supply air filter pressure drop. | 0.0 | 2000.0 | Pa
28 | SA AHU filter pressure alarm limit | Present supply air filter pressure alarm limit. | 0.0 | 2000.0 | Pa
29 | EA AHU filter pressure level | Present extract air filter pressure drop. | 0.0 | 2000.0 | Pa
30 | EA AHU filter pressure alarm limit | Present extract air filter pressure alarm limit. | 0.0 | 2000.0 | Pa
31 | SA End-filter pressure level | Present supply air end-filter pressure drop. | 0.0 | 2000.0 | Pa
32 | SA End-filter pressure alarm limit | Present supply air end-filter pressure alarm limit. | 0.0 | 2000.0 | Pa
Fans
37 | SA Fan level | Present fan speed level of the supply air fan. | 0.00 | 100.00 | %
38 | EA Fan level | Present fan speed level of the extract air fan. | 0.00 | 100.00 | %
39 | SA Fan speed | Present fan speed level of the supply air fan. | 0 | 4000 | rpm
40 | EA Fan speed | Present fan speed level of the extract air fan. | 0 | 4000 | rpm
41 | SA Voltage | Present voltage level of the supply air fan. | 0 | 500 | V
42 | EA Voltage | Present voltage level of the extract air fan. | 0 | 500 | V
43 | SA Fan current | Present current level of the supply air fans. Includes all supply air fans. | 0 | 32.700 | A
44 | EA Fan current | Present current level of the extract air fans. Includes all supply air fans. | 0 | 32.700 | A
45 | SA Fan power | Present power level of the supply air fans. Includes all supply air fans. | 0 | 45.000 | kW
46 | EA Fan power | Present power consumption level of the extract air fans. Includes all extract air fans. | 0 | 45.000 | kW
47 | SA Fan kWh | Total power consumption of the supply air fans. Includes all supply air fans. | 0 | 9999 | kWh
48 | EA Fan kWh | Total power consumption level of the extract air fans. Includes all extract air fans. | 0 | 9999 | kWh
49 | SA Fan MWh | Total power consumption of the supply air fans. Includes all supply air fans. | 0 | 9999 | MWh
50 | EA Fan MWh | Total power consumption level of the extract air fans. Includes all extract air fans. | 0 | 9999 | MWh
51 | SA Fan operation time | Total operation time of the supply air fan presented in days (24h). | 0..9999 | 9999 | days
52 | EA Fan operation time | Total operation time of the extract air fan presented in days (24h). | 0..9999 | 9999 | days
55 | SA Fan min air flow | Supply air AHU min air flow | 0 | 18000 | l/s
56 | EA Fan min air flow | Extract air AHU min air flow | 0 | 18000 | l/s
57 | SA Fan max air flow | Supply air AHU max air flow | 0 | 18000 | l/s
58 | EA Fan max air flow | Extract air AHU max air flow | 0 | 18000 | l/s
63 | SFP | Calculated SFP level. | 0.00 | 100.00 | kW/m3/s
AHU Temperature sensors
64 | SA Temperature | Present supply air temperature. | -55.00 | 125.00 | °C
65 | SA-D Temperature | Present supply air density temperature. | -55.00 | 125.00 | °C
66 | EA Temperature | Present extract air temperature in the unit (only AHU type RX). | -55.00 | 125.00 | °C
67 | EA-D Temperature | Present extract air density temperature. | -55.00 | 125.00 | °C
68 | EA Regulation temperature | Present extract air temperature used for regulation. | -55.00 | 125.00 | °C
69 | EA Temperature PX/CX | Present extract air temperature in the unit (only AHU type PX/CX). | -55.00 | 125.00 | °C |  | 1.13
70 | EA Temperature SD | Present extract air temperature in the unit (only AHU type SD). | -55.00 | 125.00 | °C |  | 1.13
72 | Outdoor temperature COOL DX | Present outdoor air temperature in the COOL DX unit. | -55.00 | 125.00 | °C |  | 1.13
73 | Outdoor temperature | Present outdoor air temperature in the unit. | -55.00 | 125.00 | °C
74 | Outdoor regulation temperature | Present outdoor air temperature used for regulation. | -55.00 | 125.00 | °C
75 | External outdoor temperature 1 | Present external outdoor temperature of sensor 1. | -55.00 | 125.00 | °C
76 | External outdoor temperature 2 | Present external outdoor temperature of sensor 2. | -55.00 | 125.00 | °C
77 | External outdoor temperature 3 | Present external outdoor temperature of sensor 3. | -55.00 | 125.00 | °C
78 | External outdoor temperature 4 | Present external outdoor temperature of sensor 4. | -55.00 | 125.00 | °C
80 | EA Duct temperature | Present extract air duct air temperature. | -55.00 | 125.00 | °C |  | 1.12
81 | Room temperature 1 | Present room temperature of sensor 1. | -55.00 | 125.00 | °C
82 | Room temperature 2 | Present room temperature of sensor 2. | -55.00 | 125.00 | °C
83 | Room temperature 3 | Present room temperature of sensor 3. | -55.00 | 125.00 | °C
84 | Room temperature 4 | Present room temperature of sensor 4. | -55.00 | 125.00 | °C
AHU Temperature regulation
87 | SA Temp regulator | Present supply air temperature regulator set point. | 0.00 | 50.00 | °C
88 | EA Temp regulator | Present extract air temperature regulator set point. | 0.00 | 50.00 | °C
90 | Cool exchanger regulator level | Present operation level of cool recovery. | 0.00 | 100.00 | % |  | 1.11
91 | Heat exchanger regulator level | Present operation level of heat recovery. | 0.00 | 100.00 | %
92 | Extra regulation sequence 1 heat regulator level | Present level of extra regulation heat. | 0.00 | 100.00 | %
93 | Extra regulation sequence 1 heat output level |  | 0.00 | 100.00 | %
94 | Reheat regulator level | Present level of reheat. | 0.00 | 100.00 | %
95 | Reheat output level |  | 0.00 | 100.00 | %
96 | ReCO2 heat level | Present level of ReCO2 heat. | 0.00 | 100.00 | %
97 | Down regulation level | Present level of fan down regulation. | 0.00 | 100.00 | %
98 | Heating boost level | Present level of heating boost. | 0.00 | 100.00 | %
99 | Extra regulation sequence 1 cool regulator level | Present level of extra regulation cool. | 0.00 | 100.00 | %
100 | Extra regulation sequence 1 cool output level | Present level of extra regulation cool. | 0.00 | 100.00 | %
101 | Cool regulator level | Present level of cooling. | 0.00 | 100.00 | %
102 | Cool output level | Present level of cooling. | 0.00 | 100.00 | %
103 | ReCO2 cool level | Present level of ReCO2 heat. | 0.00 | 100.00 | %
104 | Cooling boost level | Present level of cooling boost. | 0.00 | 100.00 | %
AHU heat exchange
105 | RHX operation level | Present speed level of the rotary heat exchanger. | 0.00 | 100.00 | %
106 | RHX/PHX/CHX efficiency | Calculated level of the heat exchanger efficiency. | 0.00 | 100.00 | % |  | 1.23
107 | RHX defrost pressure level | Present pressure drop for the rotary heat exchanger. | 0.0 | 2000.0 | Pa
108 | RHX defrost pressure alarm limit | Present pressure drop alarm limit for the rotary heat exchanger. | 0.0 | 2000.0 | Pa
109 | RHX carry over control pressure level | Present pressure difference for the rotary heat exchangers purging sector. | 0.0 | 1000.0 | Pa
111 | RHX operation time | Total operation time of the rotary heat exchanger presented in days (24h). | 0 | 9999 | Days
116 | PX defrost pressure level | PHX-2/3: Present pressure drop for the plate heat exchanger. PHX-1, one damper and humidity sensor. PHX-2, three dampers. PHX-3, one damper and pressure sensor. | 0.0 | 2000.0 | Pa |  | 1.13
117 | PHX-3D Bypass output | PHX-1: Present level of plate heat exchanger bypass output. | 0.00 | 100.00 | %
118 | PHX-3D Bypass input | PHX-1: Present level of plate heat exchanger bypass input. | 0.00 | 100.00 | %
119 | PHX-3D Bypass temperature 1 | PHX-1: Present bypass temperature sensor 1 in plate heat exchanger. | -55.00 | 125.00 | °C
120 | PHX-3D Bypass temperature 2 | PHX-1: Present bypass temperature sensor 2 in plate heat exchanger. | -55.00 | 125.00 | °C
121 | PX exchanger damper 1 output | PHX-2: Present level of plate heat exchanger damper 1 output. | 0.00 | 100.00 | % |  | 1.13
122 | PHX-2 Damper 1 input | Present level of plate heat exchanger damper 1 input. | 0.00 | 100.00 | % |  | 1.16
123 | PX exchanger damper 2 output | PHX-2: Present level of plate heat exchanger damper 2 output. | 0.00 | 100.00 | % |  | 1.13
124 | PHX-2 Damper 2 input | Present level of plate heat exchanger damper 2 input. | 0.00 | 100.00 | % |  | 1.16
125 | PX exchanger bypass output | PHX-2: Present level of plate heat exchanger bypass output. | 0.00 | 100.00 | % |  | 1.13
126 | PX exchanger bypass feedback | PHX-2: Present level of plate heat exchanger bypass input. | 0.00 | 100.00 | % |  | 1.13
127 | CHX-1 Valve output | Present level of coil heat exchanger valve output. | 0.00 | 100.00 | %
128 | CHX-1 Valve input | Present level of coil heat exchanger valve input. | 0.00 | 100.00 | %
129 | CHX-1 Return water temperature | Present return water temperature for coil heat exchanger. | -55.00 | 125.00 | °C
130 | PHX/CHX operation time | Total operation time of the coil heat exchanger presented in days (24h). | 0 | 9999 | Days
132 | PHX-1D Bypass output | PHX-3: Present level of plate heat exchanger bypass output. | 0.00 | 100.00 | % |  | 1.12
133 | PHX-1D Bypass input | PHX-3: Present level of plate heat exchanger bypass input. | 0.00 | 100.00 | % |  | 1.12
134 | CHX-2 Return water temperature | Present return water temperature for coil heat exchanger. | -55.00 | 125.00 | °C |  | 1.18
135 | CHX-2 Extract coil pressure level | Present extract coil differiential pressure. | 0 | 1600 | mBar |  | 1.18
136 | PHX/CHX Humidity level | PHX-1/2: Present level of air-humidity for calculation of bypass/valve limitation. | 0.00 | 100.00 | %
137 | CHX-2 Valve output | Present level of coil heat exchanger valve output. | 0.00 | 100.00 | % |  | 1.18
138 | CHX-2 Valve input | Present level of coil heat exchanger valve input. | 0.00 | 100.00 | % |  | 1.18
139 | CHX-2 Pump output | Present level of pump heat exchanger output | 0.00 | 100.00 | % |  | 1.18
AHU Coils
141 | Extra regulation sequence 1 anti frost temp/overheat input | Present extra regulation anti frost temperature for water heat coil. Value 0=overheat when electric heat is used. | -55.00 | 125.00 | °C
143 | Extra regulation sequence 2 anti frost temp/overheat input | Present extra regulation anti frost temperature for water heat coil. Value 0=overheat when electric heat is used. | -55.00 | 125.00 | °C |  | 1.13
146 | Extra regulation sequence 1 input level |  | 0.00 | 100.00 | %
147 | Extra regulation sequence 1 heat operation time | Total operation time of extra regulation heat presented in days (24h). | 0 | 9999 | Days
148 | Extra regulation sequence 1 cool operation time | Total operation time of extra regulation cool presented in days (24h). | 0 | 9999 | Days
149 | Extra regulation sequence 2 input level |  | 0.00 | 100.00 | % |  | 1.13
150 | Extra regulation sequence 2 heat operation time | Total operation time of extra regulation heat presented in days (24h). | 0 | 9999 | Days |  | 1.13
151 | Extra regulation sequence 2 cool operation time | Total operation time of extra regulation cool presented in days (24h). | 0 | 9999 | Days |  | 1.13
153 | Re-heat anti frost temp/overheat input | Present anti frost temperature for water heat coil. Value 0=overheat when electric heat is used. | -55.00 | 125.00 | °C
158 | Re-heat input level |  | 0.00 | 100.00 | %
159 | Re-heat operation time | Total operation time of re-heat presented in days (24h). | 0 | 9999 | Days
164 | Cool water temperature | Present cool water temperature for water cool coil. | -55.00 | 125.00 | °C
168 | Cool input level |  | 0.00 | 100.00 | %
169 | Cool operation time | Total operation time of cool presented in days (24h). | 0 | 9999 | Days
Xzone temperature sensors
174 | Xzone SA temperature | Present supply air temperature. | -55.00 | 125.00 | °C
175 | Xzone EA temperature | Present extract air temperature in the unit. | -55.00 | 125.00 | °C
176 | Xzone EA regulation temperature | Present extract air temperature used for regulation. | -55.00 | 125.00 | °C
177 | Xzone Room temperature 1 | Present room temperature of sensor 1. | -55.00 | 125.00 | °C
178 | Xzone Room temperature 2 | Present room temperature of sensor 2. | -55.00 | 125.00 | °C
179 | Xzone Room temperature 3 | Present room temperature of sensor 3. | -55.00 | 125.00 | °C
180 | Xzone Room temperature 4 | Present room temperature of sensor 4. | -55.00 | 125.00 | °C
181 | Xzone Room temperature min/max/average | Present calculated min, max or average (depending on configuration) temperature of room sensor 1-4. | -55.00 | 125.00 | °C
Xzone Temperature regulation
186 | Xzone SA Temp regulator | Present supply air temperature regulator set point. | 0.00 | 50.00 | °C
187 | Xzone EA Temp regulator | Present extract air temperature regulator set point. | 0.00 | 50.00 | °C
190 | Xzone re-heat regulator level |  | 0.00 | 100.00 | %
193 | Xzone cool regulator level |  | 0.00 | 100.00 | %
Xzone coils
199 | Xzone heat, anti frost temp/overheat input | Present Xzone heat anti frost temperature for water heat coil. Value 0=Overheat when electric heat is used. | -55.00 | 125.00 | °C
203 | Xzone heat, output level | Present level of Xzone heat output. | 0 | 100.00 | %
204 | Xzone heat, input level | Present Xzone heat input. | 0 | 100.00 | %
205 | Xzone heat, operation time | Total operation time of Xzone heat presented in days (24h). | 0 | 9999 | Days
210 | Xzone cool, water temperature |  | -55.00 | 125.00 | °C
214 | Xzone cool, output level | Present level of Xzone cool. | 0 | 100.00 | %
215 | Xzone cool, input level | Present Xzone cool valve position. | 0 | 100.00 | %
216 | Xzone cool, operation time | Total operation time of Xzone cool presented in days (24h). | 0 | 9999 | Days
Pre-heat
220 | Pre-heat temperature | Present pre-heat temperature. | -55.00 | 125.00 | °C
221 | Pre-heat temp regulator set point | Present pre-heat temperature regulator set point. | -40.00 | 40.00 | °C
222 | Pre-heat temp regulator level
225 | Pre-heat anti frost temp/overheat input | Present pre-heat anti frost temperature for water heat coil. Value 0=Overheat when electric heat is used. | -55.00 | 125.00 | °C
228 | Pre-heat output level | Present pre-heat output level. | 0.00 | 100.00 | %
229 | Pre-heat input level | Present pre-heat input level. | 0.00 | 100.00 | %
230 | Pre-heat operation time | Total operation time of pre-heat presented in days (24h). | 0 | 9999 | Days
ReCO2
233 | ReCO2 recirculation damper output | Present output signal to the recirculation damper. | 0.00 | 100.00 | %
234 | ReCO2 recirculation damper input | Present input signal from the recirculation damper. | 0.00 | 100.00 | %
235 | ReCO2 outdoor damper output | Present output signal to the outdoor air damper. | 0.00 | 100.00 | %
236 | ReCO2 outdoor damper input | Present input signal from the outdoor air damper. | 0.00 | 100.00 | %
237 | ReCO2 outdoor air flow | Present outdoor air flow level. | 0.0 | AI 57 | l/s
238 | ReCO2 outdoor air flow regulator set point | Present outdoor air flow regulator set point. | 0.0 | AI 57 | l/s
Humidity
244 | SA humidity level | Present level of supply air humidity | 0.00 | 100.00 | %RH
245 | SA humidity temperature | Present temperature inside the supply air humidity sensor. | -40.00 | 123.00 | °C
246 | SA dew point | Calculated supply air dew point. | -40.00 | 40.00 | °C
247 | EA humidity level | Present level of extract air humidity. | 0.00 | 100.00 | %RH
248 | EA humidity temperature | Present temperature inside the extract air humidity sensor. | -40.00 | 123.00 | °C
249 | EA dew point | Calculated extract air dew point. | -40.00 | 40.00 | °C
251 | Dehumidifying SA dew point regulator set point | Present supply air dew point regulator point. | -40.00 | 40.00 | °C
252 | Dehumidifying output level | Present level of the dehumidifying output. | 0.00 | 100.00 | %
254 | Humidifying SA regulator set point |  | 0.00 | 100.00 | %RH
255 | Humidifying output level | Present level of the dehumidifying output. | 0.00 | 100.00 | %
260 | Exhaust air humidity | Present level of exhaust air humidity. | 0.00 | 100.00 | %RH |  | 1.23
261 | Exhaust air temperature | Present temperature inside the exhaust air humidity sensor. | -40.00 | 123.00 | °C |  | 1.23
262 | Outdoor air humidity | Present level of outdoor air humidity. | 0.00 | 100.00 | %RH |  | 2.37
263 | Outdoor air temperature | Present temperature inside the outdoor air humidity sensor. | -40.00 | 123.00 | °C |  | 2.37
264 | Room air humidity | Present level of room air humidity. | 0.00 | 100.00 | %RH |  | 2.37
265 | Room air temperature | Present temperature inside the room air humidity sensor. | -40.00 | 123.00 | °C |  | 2.37
VOC
266 | VOC level | Present level of VOC | 450 | 10000 | ppm
267 | CO2 level | Present level of CO2 | 0 | 10000 | ppm |  | 1.23
COOL DX
271 | COOL DX, unit power size |  | 0 | 15
274 | COOL DX, compressor 1 low pressure level |  | 0 | 34.50 | Bar
275 | COOL DX, compressor 1 high pressure level |  | 0 | 45.00 | Bar
276 | COOL DX, compressor 2 low pressure level |  | 0 | 34.50 | Bar
277 | COOL DX, compressor 2 high pressure level |  | 0 | 45.00 | Bar
SMART Link
289 | SMART Link, WB outlet water 1 |  | -40.0 | 176.0 | °C
290 | SMART Link, WB outlet water 2 |  | -40.0 | 176.0 | °C
291 | SMART Link, WB outlet water 3 |  | -40.0 | 176.0 | °C
292 | SMART Link, WB outlet water 4 |  | -40.0 | 176.0 | °C
293 | SMART Link, WB outlet water average |  | -40.0 | 176.0 | °C
294 | SMART Link, WB reference water |  | -40.0 | 176.0 | °C
297 | SMART Link WB, heated water set point |  | -40.0 | 176.0 | °C
298 | SMART Link WB, chilled water set point |  | -40.0 | 176.0 | °C
299 | SMART Link WB, Min heated water set point |  | -40.0 | 176.0 | °C
300 | SMART Link WB, Max heated water set point |  | -40.0 | 176.0 | °C
301 | SMART Link WB, Min chilled water set point |  | -40.0 | 176.0 | °C
302 | SMART Link WB, Max chilled water set point |  | -40.0 | 176.0 | °C
327 | SMART Link, DX unit 1 power level set point |  | 0 | 100.00 | %
328 | SMART Link, DX unit 1 power level |  | 0 | 100.00 | %
329 | SMART Link, DX unit 1 operation time |  | 0 | 9999 | Days
338 | SMART Link, DX unit 2 power level set point |  | 0 | 100.00 | %
339 | SMART Link, DX unit 2 power level |  | 0 | 100.00 | %
340 | SMART Link, DX unit 2 operation time |  | 0 | 9999 | Days
349 | SMART Link, DX unit 3 power level set point |  | 0 | 100.00 | %
350 | SMART Link, DX unit 3 power level |  | 0 | 100.00 | %
351 | SMART Link, DX unit 3 operation time |  | 0 | 9999 | Days
360 | SMART Link, DX unit 4 power level set point |  | 0 | 100.00 | %
361 | SMART Link, DX unit 4 power level |  | 0 | 100.00 | %
362 | SMART Link, DX unit 4 operation time |  | 0 | 9999 | Days
AYC
374 | AYC Heat, heated water | Present heat temperature. | -55.00 | 125.00 | °C
375 | AYC Heated water set point | Present heat temperature regulator set point. | 0 | 100.00 | °C
376 | AYC Heat, valve output | Present level of the heat valve output. | 0 | 100.00 | %
377 | AYC Heat, valve input | Present level of the heat valve input. | 0 | 100.00 | %
378 | AYC Heat, operation time | Total operation time of AYC heat presented in days (24h). | 0 | 9999 | Days
379 | AYC Heated water heat demand |  | 0 | 100.00 | %
387 | AYC Cool, chilled water | Present cool temperature. | -55.00 | 125.00 | °C
388 | AYC Chilled water set point | Present cool temperature regulator set point. | 0 | 100.00 | °C
389 | AYC Cool, valve output | Present cool of the heat valve output. | 0 | 100.00 | %
390 | AYC Cool, valve input | Present cool of the heat valve input. | 0 | 100.00 | %
391 | AYC Cool, operation time | Total operation time of AYC cool presented in days (24h). | 0 | 9999 | Days
392 | AYC Chilled water cool demand |  | 0 | 100.00 | %
MIRU Control
400 | MIRU Control 1 Min air flow | Min possible air flow setting | 0 | 10000 | l/s
401 | MIRU Control 1 Max air flow | Max possible air flow setting | 0 | 10000 | l/s
402 | MIRU Control 1 Air flow | Present air flow. | 0 | 1000 | l/s
403 | MIRU Control 1 Air flow set point | Present air flow regulator set point. | 0 | 1000 | l/s
404 | MIRU Control 1 Pressure | Present duct pressure. | 0 | 750 | Pa
405 | MIRU Control 1 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
406 | MIRU Control 1 External temperature | Present external temperature. | -55.00 | 95.00 | °C
407 | MIRU Control 1 Operation time | Present operation time, present in days (24h). | 0 | 9999 | Days
408 | MIRU Control 1 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
409 | MIRU Control 1 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
410 | MIRU Control 1 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
411 | MIRU Control 1 kWh | kWh value. | 0 | 9999 | kWh
412 | MIRU Control 1 MWh | MWh value. | 0 | 32000 | MWh
417 | MIRU Control 2 Min air flow | Min possible air flow setting | 0 | 10000 | l/s
418 | MIRU Control 2 Max air flow | Max possible air flow setting | 0 | 10000 | l/s
419 | MIRU Control 2 Air flow | Present air flow. | 0 | 1000 | l/s
420 | MIRU Control 2 Air flow set point | Present air flow regulator set point. | 0 | 1000 | l/s
421 | MIRU Control 2 Pressure | Present duct pressure. | 0 | 750 | Pa
422 | MIRU Control 2 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
423 | MIRU Control 2 External temperature | Present external temperature. | -55.00 | 95.00 | °C
424 | MIRU Control 2 Operation time | Present operation time, present in days (24h). | 0 | 9999 | Days
425 | MIRU Control 2 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
426 | MIRU Control 2 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
427 | MIRU Control 2 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
428 | MIRU Control 2 kWh | kWh value. | 0 | 9999 | kWh
429 | MIRU Control 2 MWh | MWh value. | 0 | 32000 | MWh
434 | MIRU Control 3 Min air flow | Min possible air flow setting | 0 | 10000 | l/s
435 | MIRU Control 3 Max air flow | Max possible air flow setting | 0 | 10000 | l/s
436 | MIRU Control 3 Air flow | Present air flow. | 0 | 1000 | l/s
437 | MIRU Control 3 Air flow set point | Present air flow regulator set point. | 0 | 1000 | l/s
438 | MIRU Control 3 Pressure | Present duct pressure. | 0 | 750 | Pa
439 | MIRU Control 3 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
440 | MIRU Control 3 External temperature | Present external temperature. | -55.00 | 95.00 | °C
441 | MIRU Control 3 Operation time | Present operation time, present in days (24h). | 0 | 9999 | Days
442 | MIRU Control 3 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
443 | MIRU Control 3 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
444 | MIRU Control 3 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
445 | MIRU Control 3 kWh | kWh value. | 0 | 9999 | kWh
446 | MIRU Control 3 MWh | MWh value. | 0 | 32000 | MWh
451 | MIRU Control 4 Min air flow | Min possible air flow setting | 0 | 10000 | l/s
452 | MIRU Control 4 Max air flow | Max possible air flow setting | 0 | 10000 | l/s
453 | MIRU Control 4 Air flow | Present air flow. | 0 | 1000 | l/s
454 | MIRU Control 4 Air flow set point | Present air flow regulator set point. | 0 | 1000 | l/s
455 | MIRU Control 4 Pressure | Present duct pressure. | 0 | 750 | Pa
456 | MIRU Control 4 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
457 | MIRU Control 4 External temperature | Present external temperature. | -55.00 | 95.00 | °C
458 | MIRU Control 4 Operation time | Present operation time, present in days (24h). | 0 | 9999 | Days
459 | MIRU Control 4 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
460 | MIRU Control 4 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
461 | MIRU Control 4 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
462 | MIRU Control 4 kWh | kWh value. | 0 | 9999 | kWh
463 | MIRU Control 4 MWh | MWh value. | 0 | 32000 | MWh
468 | MIRU Control 5 Min air flow | Min possible air flow setting | 0 | 10000 | l/s
469 | MIRU Control 5 Max air flow | Max possible air flow setting | 0 | 10000 | l/s
470 | MIRU Control 5 Air flow | Present air flow. | 0 | 1000 | l/s
471 | MIRU Control 5 Air flow set point | Present air flow regulator set point. | 0 | 1000 | l/s
472 | MIRU Control 5 Pressure | Present duct pressure. | 0 | 750 | Pa
473 | MIRU Control 5 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
474 | MIRU Control 5 External temperature | Present external temperature. | -55.00 | 95.00 | °C
475 | MIRU Control 5 Operation time | Present operation time, present in days (24h). | 0 | 9999 | Days
476 | MIRU Control 5 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
477 | MIRU Control 5 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
478 | MIRU Control 5 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
479 | MIRU Control 5 kWh | kWh value. | 0 | 9999 | kWh
480 | MIRU Control 5 MWh | MWh value. | 0 | 32000 | MWh
485 | MIRU Control 6 Min air flow | Min possible air flow setting | 0 | 10000 | l/s
486 | MIRU Control 6 Max air flow | Max possible air flow setting | 0 | 10000 | l/s
487 | MIRU Control 6 Air flow | Present air flow. | 0 | 1000 | l/s
488 | MIRU Control 6 Air flow set point | Present air flow regulator set point. | 0 | 1000 | l/s
489 | MIRU Control 6 Pressure | Present duct pressure. | 0 | 750 | Pa
490 | MIRU Control 6 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
491 | MIRU Control 6 External temperature | Present external temperature. | -55.00 | 95.00 | °C
492 | MIRU Control 6 Operation time | Present operation time, present in days (24h). | 0 | 9999 | Days
493 | MIRU Control 6 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
494 | MIRU Control 6 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
495 | MIRU Control 6 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
496 | MIRU Control 6 kWh | kWh value. | 0 | 9999 | kWh
497 | MIRU Control 6 MWh | MWh value. | 0 | 32000 | MWh
502 | MIRU Control 7 Min air flow | Min possible air flow setting | 0 | 10000 | l/s
503 | MIRU Control 7 Max air flow | Max possible air flow setting | 0 | 10000 | l/s
504 | MIRU Control 7 Air flow | Present air flow. | 0 | 1000 | l/s
505 | MIRU Control 7 Air flow set point | Present air flow regulator set point. | 0 | 1000 | l/s
506 | MIRU Control 7 Pressure | Present duct pressure. | 0 | 750 | Pa
507 | MIRU Control 7 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
508 | MIRU Control 7 External temperature | Present external temperature. | -55.00 | 95.00 | °C
509 | MIRU Control 7 Operation time | Present operation time, present in days (24h). | 0 | 9999 | Days
510 | MIRU Control 7 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
511 | MIRU Control 7 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
512 | MIRU Control 7 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
513 | MIRU Control 7 kWh | kWh value. | 0 | 9999 | kWh
514 | MIRU Control 7 MWh | MWh value. | 0 | 32000 | MWh
519 | MIRU Control 8 Min air flow | Min possible air flow setting | 0 | 10000 | l/s
520 | MIRU Control 8 Max air flow | Max possible air flow setting | 0 | 10000 | l/s
521 | MIRU Control 8 Air flow | Present air flow. | 0 | 1000 | l/s
522 | MIRU Control 8 Air flow set point | Present air flow regulator set point. | 0 | 1000 | l/s
523 | MIRU Control 8 Pressure | Present duct pressure. | 0 | 750 | Pa
524 | MIRU Control 8 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
525 | MIRU Control 8 External temperature | Present external temperature. | -55.00 | 95.00 | °C
526 | MIRU Control 8 Operation time | Present operation time, present in days (24h). | 0 | 9999 | Days
527 | MIRU Control 8 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
528 | MIRU Control 8 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
529 | MIRU Control 8 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
530 | MIRU Control 8 kWh | kWh value. | 0 | 9999 | kWh
531 | MIRU Control 8 MWh | MWh value. | 0 | 32000 | MWh
536 | MIRU Control 9 Min air flow | Min possible air flow setting | 0 | 10000 | l/s
537 | MIRU Control 9 Max air flow | Max possible air flow setting | 0 | 10000 | l/s
538 | MIRU Control 9 Air flow | Present air flow. | 0 | 1000 | l/s
539 | MIRU Control 9 Air flow set point | Present air flow regulator set point. | 0 | 1000 | l/s
540 | MIRU Control 9 Pressure | Present duct pressure. | 0 | 750 | Pa
541 | MIRU Control 9 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
542 | MIRU Control 9 External temperature | Present external temperature. | -55.00 | 95.00 | °C
543 | MIRU Control 9 Operation time | Present operation time, present in days (24h). | 0 | 9999 | Days
544 | MIRU Control 9 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
545 | MIRU Control 9 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
546 | MIRU Control 9 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
547 | MIRU Control 9 kWh | kWh value. | 0 | 9999 | kWh
548 | MIRU Control 9 MWh | MWh value. | 0 | 32000 | MWh
553 | MIRU Control 10 Min air flow | Min possible air flow setting | 0 | 10000 | l/s
554 | MIRU Control 10 Max air flow | Max possible air flow setting | 0 | 10000 | l/s
555 | MIRU Control 10 Air flow | Present air flow. | 0 | 1000 | l/s
556 | MIRU Control 10 Air flow set point | Present air flow regulator set point. | 0 | 1000 | l/s
557 | MIRU Control 10 Pressure | Present duct pressure. | 0 | 750 | Pa
558 | MIRU Control 10 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
559 | MIRU Control 10 External temperature | Present external temperature. | -55.00 | 95.00 | °C
560 | MIRU Control 10 Operation time | Present operation time, present in days (24h). | 0 | 9999 | Days
561 | MIRU Control 10 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
562 | MIRU Control 10 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
563 | MIRU Control 10 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
564 | MIRU Control 10 kWh | kWh value. | 0 | 9999 | kWh
565 | MIRU Control 10 MWh | MWh value. | 0 | 32000 | MWh
Software
570 | IQlogic software version | Present controller software version | 0.00 | 99.00
Alarms
604 | Triggered alarm #1 | ((Alarm group - 1) x 15) + alarm number in group=Triggered alarm number. Zero if no triggered alarm. | 0 | 1500
605 | Triggered alarm #2 |  | 0 | 1500
606 | Triggered alarm #3 |  | 0 | 1500
607 | Triggered alarm #4 |  | 0 | 1500
608 | Triggered alarm #5 |  | 0 | 1500
609 | Triggered alarm #6 |  | 0 | 1500
610 | Triggered alarm #7 |  | 0 | 1500
611 | Triggered alarm #8 |  | 0 | 1500
612 | Triggered alarm #9 |  | 0 | 1500
613 | Triggered alarm #10 |  | 0 | 1500
614 | Triggered alarm group #1 | Zero if no triggered alarm group. | 0 | 100
615 | Triggered alarm group #2 |  | 0 | 100
616 | Triggered alarm group #3 |  | 0 | 100
617 | Triggered alarm group #4 |  | 0 | 100
618 | Triggered alarm group #5 |  | 0 | 100
619 | Triggered alarm group #6 |  | 0 | 100
620 | Triggered alarm group #7 |  | 0 | 100
621 | Triggered alarm group #8 |  | 0 | 100
622 | Triggered alarm group #9 |  | 0 | 100
623 | Triggered alarm group #10 |  | 0 | 100
Time schedule
661 | Prolonged low speed remaining hours | Prolonged external low speed remaining operation. | 0 | 23 |  |  | 1.13
662 | Prolonged low speed remaining seconds | Prolonged external low speed remaining operation. | 0 | 3600 |  |  | 1.13
663 | Prolonged high speed remaining hours | Prolonged external high speed remaining operation. | 0 | 23 |  |  | 1.13
664 | Prolonged high speed remaining seconds | Prolonged external high speed remaining operation. | 0 | 3600 |  |  | 1.13
Reserved
700 | Extra regulation sequence 2 heat regulator level | Present level of extra regulation heat. | 0.00 | 100.00 | % |  | 1.13
701 | Extra regulation sequence 2 heat output level | Present level of extra regulation heat. | 0.00 | 100.00 | % |  | 1.13
702 | Extra regulation sequence 2 cool regulator level | Present level of extra regulation cool. | 0.00 | 100.00 | % |  | 1.13
703 | Extra regulation sequence 2 cool output level | Present level of extra regulation cool. | 0.00 | 100.00 | % |  | 1.13
704 | Re-heat retention at stop |  | 0.00 | 40.00 | °C |  | 1.20
705 | Re-heat retention at operation |  | 0.00 | 40.00 | °C |  | 1.20
706 | Re-heat frost protection alarm limit |  | 0.00 | 40.00 | °C |  | 1.20
707 | Pre-heat retention at stop |  | 0.00 | 40.00 | °C |  | 1.20
708 | Pre-heat retention at operation |  | 0.00 | 40.00 | °C |  | 1.20
709 | Pre-heat frost protection alarm limit |  | 0.00 | 40.00 | °C |  | 1.20
710 | Xzone heat retention at stop |  | 0.00 | 40.00 | °C |  | 1.20
711 | Xzone heat retention at operation |  | 0.00 | 40.00 | °C |  | 1.20
712 | Xzone frost protection alarm limit |  | 0.00 | 40.00 | °C |  | 1.20
713 | Extra regulation sequence 1 heat retention at stop |  | 0.00 | 40.00 | °C |  | 1.20
714 | Extra regulation sequence 1 heat retention at operation |  | 0.00 | 40.00 | °C |  | 1.20
715 | Extra regulation sequence 1 frost protection alarm limit |  | 0.00 | 40.00 | °C |  | 1.20
716 | Extra regulation sequence 2 heat retention at stop |  | 0.00 | 40.00 | °C |  | 1.20
717 | Extra regulation sequence 2 heat retention at operation |  | 0.00 | 40.00 | °C |  | 1.20
718 | Extra regulation sequence 2 frost protection alarm limit |  | 0.00 | 40.00 | °C |  | 1.20
Energy monitoring
719 | Heat exchange motor power consumption W |  | 0 | 10000 | W |  | 1.28
720 | Heat exchange motor power consumption kW |  | 0.000 | 10.000 | kW |  | 1.28
721 | Heat exchange motor energy consumption kWh |  | 0 | 999 | kWh |  | 1.28
722 | Heat exchange motor energy consumption MWh |  | 0 | 30000 | MWh |  | 1.28
723 | Heat power recovery W |  | -999 | 999 | W |  | 1.28
724 | Heat power recovery kW |  | -30000 | 30000 | kW |  | 1.28
725 | Heat power consumption W |  | -999 | 999 | W |  | 1.28
726 | Heat power consumption kW |  | -30000 | 30000 | kW |  | 1.28
727 | Cool power recovery W |  | -999 | 999 | W |  | 1.28
728 | Cool power recovery kW |  | -30000 | 30000 | kW |  | 1.28
729 | Cool power consumption W |  | -999 | 999 | W |  | 1.28
730 | Cool power consumption kW |  | -30000 | 30000 | kW |  | 1.28
731 | Heat energy recovery kWh |  | 0 | 999 | kWh |  | 1.28
732 | Heat energy recovery MWh |  | 0 | 30000 | MWh |  | 1.28
733 | Cool energy recovery kWh |  | 0 | 999 | kWh |  | 1.28
734 | Cool energy recovery MWh |  | 0 | 30000 | MWh |  | 1.28
735 | Heat energy consumption kWh |  | 0 | 999 | kWh |  | 1.28
736 | Heat energy consumption MWh |  | 0 | 30000 | MWh |  | 1.28
737 | Cool energy consumption kWh |  | 0 | 999 | kWh |  | 1.28
738 | Cool energy consumption MWh |  | 0 | 30000 | MWh |  | 1.28
739 | Pulse counter input 1 kWh |  | 0 | 999 | kWh |  | 2.36
740 | Pulse counter input 1 MWh |  | 0 | 30000 | MWh |  | 2.36
741 | Pulse counter input 2 kWh |  | 0 | 999 | kWh |  | 2.36
742 | Pulse counter input 2 MWh |  | 0 | 30000 | MWh |  | 2.36
743 | Pulse counter input 3 kWh |  | 0 | 999 | kWh |  | 2.36
744 | Pulse counter input 3 MWh |  | 0 | 30000 | MWh |  | 2.36
745 | Pulse counter input 4 kWh |  | 0 | 999 | kWh |  | 2.36
746 | Pulse counter input 4 MWh |  | 0 | 30000 | MWh |  | 2.36
BMS I/O-modules
800 | External operation I/O-module 3, analogue input 1 |  | 0.00 | 100.00 | % |  | 1.20
801 | External operation I/O-module 3, analogue input 2 |  | 0.00 | 100.00 | % |  | 1.20
804 | External operation I/O-module 3, analogue output 1 |  | 0.00 | 100.00 | % |  | 1.20
805 | External operation I/O-module 3, analogue output 2 |  | 0.00 | 100.00 | % |  | 1.20
806 | External operation I/O-module 6, analogue input 1 |  | 0.00 | 100.00 | % |  | 1.20
807 | External operation I/O-module 6, analogue input 2 |  | 0.00 | 100.00 | % |  | 1.20
810 | External operation I/O-module 6, analogue output 1 |  | 0.00 | 100.00 | % |  | 1.20
811 | External operation I/O-module 6, analogue output 2 |  | 0.00 | 100.00 | % |  | 1.20
812 | External operation I/O-module A, analogue input |  | 0.00 | 100.00 | % |  | 1.20
813 | External operation I/O-module A, temp sensor 1 |  | -55.00 | 125.00 | °C |  | 1.20
814 | External operation I/O-module A, temp sensor 2 |  | -55.00 | 125.00 | °C |  | 1.20
815 | External operation I/O-module B, analogue input |  | 0.00 | 100.00 | % |  | 1.20
816 | External operation I/O-module B, temp sensor 1 |  | -55.00 | 125.00 | °C |  | 1.20
817 | External operation I/O-module B, temp sensor 2 |  | -55.00 | 125.00 | °C |  | 1.20
818 | External operation I/O-module C, analogue input |  | 0.00 | 100.00 | % |  | 1.20
819 | External operation I/O-module C, temp sensor 1 |  | -55.00 | 125.00 | °C |  | 1.20
820 | External operation I/O-module C, temp sensor 2 |  | -55.00 | 125.00 | °C |  | 1.20
H/C
1405 | H/C recirculation defrost damper output |  | 0.00 | 100.00 | % |  | 1.23
1406 | H/C recirculation defrost damper input |  | 0.00 | 100.00 | % |  | 1.23
1409 | H/C heat anti frost temp/overheat input | Present H/C heat anti frost temperature for water heat coil. Value 0=overheat when electric heat is used. | -55.00 | 125.00 | °C |  | 1.23
1413 | H/C operation level |  | 0.00 | 100.00 | % |  | 1.23
1414 | H/C heat defrost level |  | 0.00 | 100.00 | % |  | 1.23
1415 | H/C defrost pressure level |  | -500.0 | 2500.0 | Pa |  | 1.23
1416 | H/C defrost pressure start limit |  | 0.0 | 1000.0 | Pa |  | 1.23
1417 | H/C defrost pressure end limit |  | 0.0 | 1000.0 | Pa |  | 1.23
1418 | H/C superheat temp |  | 0.0 | 99.0 | K |  | 1.23
1419 | H/C discharge temp |  | -10.0 | 130.0 | °C |  | 1.23
1420 | H/C suction temp |  | -40.0 | 105.0 | °C |  | 1.23
1421 | H/C condensation temp |  | 0.0 | 1000.0 | °C |  | 1.23
1422 | H/C evaporation temp |  | 0.0 | 1000.0 | °C |  | 1.23
1423 | H/C high pressure |  | 0.10 | 50.00 | Bar |  | 1.23
1424 | H/C low pressure |  | 0.10 | 50.00 | Bar |  | 1.23
External override
3002 | External override, remaining time |  | 0 | 4320 | min |  | 1.30

## Analog Output
GOLD_E_F_BACnet_230307
Analog Output (R/W).
Object Instance | Object Name | Description | Min | Max | Unit | Default | Misc
1 | Extract air start up | Extract air start up flow. | AI 56 | AI 58 | l/s

## Analog Value
GOLD_E_F_BACnet_230307
Analog Value (R/W).
Object Instance | Object Name | Description | Min | Max | Unit | Default | Misc
AHU fan regulation
3 | SA low speed air flow set point | Supply air flow set point for the unit when running in low speed operation. | 0 | AV 5 | l/s
4 | EA low speed air flow set point | Extract air flow set point for the unit when running in low speed operation. | 0 | AV 6 | l/s
5 | SA high speed air flow set point | Supply air flow set point for the unit when running in high speed operation. | AV 3 | AV 7 | l/s
6 | EA high speed air flow set point | Extract air flow set point for the unit when running in high speed operation. | AV 4 | AV 8 | l/s
7 | SA max speed air flow set point | Supply air flow max. limit for the unit when the low/high speed operation set point is altered by boosting function etc. | AV 5 | AI 57 | l/s
8 | EA max speed air flow set point | Extract air flow max. limit for the unit when the low/high speed operation set point is altered by boosting function etc. | AV 6 | AI 58 | l/s
9 | SA regulation zone | Supply air flow regulation zone setting in % of the present air flow set point that the regulator is allowed to work within. | 1.00 | 40.00 | % | 20.00
10 | EA regulation zone | Extract air flow regulation zone setting in % of the present air flow set point that the regulator is allowed to work within. | 1.00 | 40.00 | % | 20.00
11 | SA regulation I-time | Supply air flow regulator affection setting. | 1 | 1800 | s | 40
12 | EA regulation I-time | Extract air flow regulator affection setting. | 1 | 1800 | s | 40
Pressure regulation
19 | SA low speed pressure set point | Supply air duct pressure set point for the unit when running in low speed operation. | 0.0 | AV 21 | Pa
20 | EA low speed pressure set point | Extract air duct pressure set point for the unit when running in low speed operation. | 0.0 | AV 22 | Pa
21 | SA high speed pressure set point | Supply air duct pressure for the unit when running in high speed operation. | AV 19 | AV 23 | Pa
22 | EA high speed pressure set point | Extract air duct pressure set point for the unit when running in high speed operation. | AV 20 | AV 24 | Pa
23 | SA max speed pressure set point | Supply air duct pressure max. limit for the unit when the low/high speed operation set point is altered by boosting function etc. | AV 21 | 750.0 | Pa
24 | EA max speed pressure set point | Extract air duct pressure max. limit for the unit when the low/high speed operation set point is altered by boosting function etc. | AV 22 | 750.0 | Pa
25 | SA max speed output signal | Max. limit for the supply air fan speed when running in pressure regulation mode. | 0 | 100.00 | %
26 | EA max speed output signal | Max. limit for the extract air fan speed when running in pressure regulation mode. | 0 | 100.00 | %
27 | SA pressure regulation zone | Supply air pressure regulation zone setting in % of the present duct pressure set point that the regulator is allowed to work within. | 1 | 40.00 | % | 15
28 | EA pressure regulation zone | Extract air pressure regulation zone setting in % of the present duct pressure set point that the regulator is allowed to work within. | 1 | 40.00 | % | 15
29 | SA pressure I-time | Supply air pressure regulator affection setting. | 0 | 1800 | s | 30
30 | EA pressure I-time | Extract air pressure regulator affection setting. | 0 | 1800 | s | 30
Demand regulation
33 | Demand low speed CO2 set point | Set point for the CO2 input signal for the unit when running in low speed operation. | 0 | 10000 | ppm | 1000 | 1.23
34 | Demand high speed CO2 set point | Set point for the CO2 input signal for the unit when running in high speed operation. | 0 | 10000 | ppm | 750 | 1.23
35 | Demand low speed VOC set point | Set point for the VOC input signal for the unit when running in low speed operation. | 0 | 10000 | ppm | 2500 | 1.23
36 | Demand high speed VOC set point | Set point for the VOC input signal for the unit when running in high speed operation. | 0 | 10000 | ppm | 1500 | 1.23
37 | Demand low speed set point | Set point for the 0..10V input signal for the unit when running in low speed operation. | 0.00 | 100.00 | % | 50.00 | 1.23
38 | Demand high speed set point | Set point for the 0..10V input signal for the unit when running in high speed operation. | 10.00 | 100.00 | % | 25.00 | 1.23
39 | SA min speed air flow set point | Supply air flow min. limit for the unit when the low/high speed operation set point is altered when running in fan regulation mode demand. | AI 55 | AV 41 | l/s
40 | EA min speed air flow set point | Extract air flow min. limit for the unit when the low/high speed operation set point is altered when running in fan regulation mode demand. | AI 56 | AV 42 | l/s
41 | SA max speed air flow set point | Supply air flow max limit for the unit when the low/high speed operation set point is altered when running in fan regulation mode demand. | AV 39 | AI 57 | l/s
42 | EA max speed air flow set point | Extract air flow max. limit for the unit when the low/high speed operation set point is altered when running in fan regulation mode demand. | AV 40 | AI 58 | l/s
43 | Demand P-band | Demand regulator P-band setting. | 1.00 | 100.00 | % | 40.00 | 1.23
44 | Demand I-time | Demand regulator affection setting. | 1 | 1800 | s | 1200 | 1.23
45 | Demand CO2 P-band | Demand C02 regulator P-band setting. | 0 | 10000 | ppm | 600 | 1.23
46 | Demand VOC P-band | Demand VOC regulator P-band setting. | 0 | 10000 | ppm | 1000 | 1.23
Slave controlled regulation
50 | Slave offset factor |  | 50.00 | 200.00 | % | 0.00
51 | SA slave offset air flow |  | - AI 57 | AI 57 | l/s | 0 | 1.31
52 | EA slave offset air flow |  | - AI 58 | AI 58 | l/s | 0 | 1.31
Fans OA temp compensation
54 | Outdoor temp compensation X1 |  | -50.00 | AV 55 | °C | -20.00
55 | Outdoor temp compensation X2 |  | AV 54 | AV 56 | °C | -10.00
56 | Outdoor temp compensation X3 |  | AV 55 | AV 57 | °C | 10.00
57 | Outdoor temp compensation X4 |  | AV 56 | 50.00 | °C | 20.00
58 | Outdoor temp compensation Y1 SA air flow |  | AI 55 | AI 57 | l/s
59 | Outdoor temp compensation Y2 SA air flow |  | AI 55 | AI 57 | l/s
60 | Outdoor temp compensation Y3 SA air flow |  | AI 55 | AI 57 | l/s
61 | Outdoor temp compensation Y4 SA air flow |  | AI 55 | AI 57 | l/s
62 | Outdoor temp compensation Y1 EA air flow |  | AI 56 | AI 58 | l/s
63 | Outdoor temp compensation Y2 EA air flow |  | AI 56 | AI 58 | l/s
64 | Outdoor temp compensation Y3 EA air flow |  | AI 56 | AI 58 | l/s
65 | Outdoor temp compensation Y4 EA air flow |  | AI 56 | AI 58 | l/s
66 | Outdoor temp compensation Y1 SA pressure |  | 20.0 | 750.0 | Pa | 100.0
67 | Outdoor temp compensation Y2 SA pressure |  | 20.0 | 750.0 | Pa | 100.0
68 | Outdoor temp compensation Y3 SA pressure |  | 20.0 | 750.0 | Pa | 100.0
69 | Outdoor temp compensation Y4 SA pressure |  | 20.0 | 750.0 | Pa | 100.0
70 | Outdoor temp compensation Y1 EA pressure |  | 20.0 | 750.0 | Pa | 100.0
71 | Outdoor temp compensation Y2 EA pressure |  | 20.0 | 750.0 | Pa | 100.0
72 | Outdoor temp compensation Y3 EA pressure |  | 20.0 | 750.0 | Pa | 100.0
73 | Outdoor temp compensation Y4 EA pressure |  | 20.0 | 750.0 | Pa | 100.0
Fans down regulation
79 | Down regulation neutral zone |  | 0.00 | 10.00 | K | 0.00
80 | Down regulation P-band |  | 1.00 | 10.00 | K | 7.00
81 | Down regulation I-time |  | 1 | 1800 | s | 60
Fans in operation at active fire alarm
85 | SA fan speed at fire alarm 1 |  | 0.00 | 100.00 | % | 100.00
86 | EA fan speed at fire alarm 1 |  | 0.00 | 100.00 | % | 100.00
88 | SA fan speed at fire alarm 2 |  | 10.00 | 100.00 | % | 100.00
89 | EA fan speed at fire alarm 2 |  | 10.00 | 100.00 | % | 100.00
91 | SA fan speed at internal fire alarm |  | 10.00 | 100.00 | % | 100.00
92 | EA fan speed at internal fire alarm |  | 10.00 | 100.00 | % | 100.00
Filters
97 | SA pre-filter alarm limit |  | 30.0 | 500.0 | Pa | 100.0
98 | EA pre-filter alarm limit |  | 30.0 | 500.0 | Pa | 100.0
103 | SA AHU-filter alarm limit |  | 30.0 | 500.0 | Pa | 100.0
104 | EA AHU-filter alarm limit |  | 30.0 | 500.0 | Pa | 100.0
109 | SA end-filter alarm limit |  | 30.0 | 500.0 | Pa | 100.0
Seasonal controlled temperature regulation
113 | Seasonal controlled temperature regulation active |  | -20.00 | 40.00 | °C | 0.00 | 1.23
114 | Seasonal controlled temperature regulation inactive |  | -20.00 | 40.00 | °C | 20.00 | 1.23
ERS-1 reg.
117 | ERS 1 step | Curve setting according to the diagram for ERS 1. | 1 | 4 |  | 2
118 | ERS 1 diff | Supply air temp difference setting according to the diagram for ERS 1. | 1.00 | 7.00 | K | 2.00
119 | ERS 1 breakpoint | Breakpoint temp setting according to the diagram for ERS 1. | 12.00 | 26.00 | °C | 22.00
ERS-2 reg.
122 | ERS 2 breakpoint X1 | Breakpoint X1 setting according to the diagram for ERS 2. | 10.00 | AV 123 | °C | 15.00
123 | ERS 2 breakpoint X2 | Breakpoint X2 setting according to the diagram for ERS 2. | AV 122 | AV 124 | °C | 20.00
124 | ERS 2 breakpoint X3 | Breakpoint X3 setting according to the diagram for ERS 2. | AV 123 | AV 125 | °C | 22.00
125 | ERS 2 breakpoint X4 | Breakpoint X4 setting according to the diagram for ERS 2. | AV 124 | 40.00 | °C | 24.00
126 | ERS 2 breakpoint Y1 | Breakpoint Y1 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 20.00
127 | ERS 2 breakpoint Y2 | Breakpoint Y2 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 18.00
128 | ERS 2 breakpoint Y3 | Breakpoint Y3 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 14.00
129 | ERS 2 breakpoint Y4 | Breakpoint Y4 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 12.00
SA Reg.
132 | SA temperature set point | Supply air temperature setting, for supply air temp regulation mode. | 10.00 | 40.00 | °C | 21.00
EA Reg.
135 | EA/Room temperature set point | Extract air/room temperature setting, for Extract air/room temp regulation mode. | 10.00 | 40.00 | °C | 21.00
136 | SA min temp set point | Supply air min. set point during EA/room regulation mode. | 8.00 | 30.00 | °C | 16.00
137 | SA max temp set point | Supply air max. set point during EA/room regulation mode. | 8.00 | 50.00 | °C | 28.00 | 1.18
138 | EA regultaion P-band |  | 1.00 | 20.00 | K | 5.00
139 | EA regultaion I-time |  | 1 | 21600 | s | 180
ORS Reg.
142 | ORS breakpoint X1 | Breakpoint X1 setting according to the diagram for ORS. | -5.00 | AV 143 | °C | -20.00
143 | ORS breakpoint X2 | Breakpoint X2 setting according to the diagram for ORS. | AV 142 | AV 144 | °C | -10.00
144 | ORS breakpoint X3 | Breakpoint X3 setting according to the diagram for ORS. | AV 143 | AV 145 | °C | 10.00
145 | ORS breakpoint X4 | Breakpoint X4 setting according to the diagram for ORS. | AV 144 | 50.00 | °C | 20.00
146 | ORS breakpoint Y1 | Breakpoint Y1 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
147 | ORS breakpoint Y2 | Breakpoint Y2 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
148 | ORS breakpoint Y3 | Breakpoint Y3 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
149 | ORS breakpoint Y4 | Breakpoint Y4 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
ORE Reg.
152 | ORE breakpoint X1 | Breakpoint X1 setting according to the diagram for ORE. | -5.00 | AV 153 | °C | -20.00
153 | ORE breakpoint X2 | Breakpoint X2 setting according to the diagram for ORE. | AV 152 | AV 154 | °C | -10.00
154 | ORE breakpoint X3 | Breakpoint X3 setting according to the diagram for ORE. | AV 153 | AV 155 | °C | 10.00
155 | ORE breakpoint X4 | Breakpoint X4 setting according to the diagram for ORE. | AV 154 | 50.00 | °C | 20.00
156 | ORE breakpoint Y1 | Breakpoint Y1 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
157 | ORE breakpoint Y2 | Breakpoint Y2 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
158 | ORE breakpoint Y3 | Breakpoint Y3 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
159 | ORE breakpoint Y4 | Breakpoint Y4 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
AHU external sensors
168 | External room temp from BMS |  | -55.00 | 125.00 | °C | 0.00
169 | External room temp from BMS alarm time |  | 0 | 9999 | min | 5
178 | External OA temp from BMS |  | -55.00 | 125.00 | °C | 0.00
179 | External OA temp from BMS alarm time |  | 0 | 9999 | min | 5
AHU Heat exchange
184 | RHX defrost start limit |  | 30.0 | 100.0 | Pa | 50.0
188 | RHX sorption rotor function | Moved to Multistate Value 188 | 0 | 2 |  | 0 | 1.16
191 | RHX min exhaust air temp set point |  | -40.00 | 20.00 | °C | 5.00
192 | RHX min exhaust air temp P-band |  | 1.00 | 40.00 | K | 8.00
193 | RHX min exhaust air temp I-time |  | 0 | 30000 | s | 30
199 | PHX periodic operation interval |  | 0 | 168 | h | 24
200 | PHX periodic operation time |  | 0 | 60 | min | 3
207 | CHX periodic operation interval |  | 0 | 168 | h | 24
208 | CHX periodic operation time |  | 0 | 60 | min | 3
213 | PHX/CHX Bypass defrost limit | PHX is default 3°C, CHX is default 5°C. | -10.00 | 5.00 | °C
214 | PHX/CHX Bypass defrost P-band |  | 1.00 | 40.00 | K | 20.00
215 | PHX/CHX Bypass defrost I-time |  | 1 | 600 | s | 60
220 | Heat exchange temperature regulation P-band |  | 1.00 | 40.00 | K | 7.00
221 | Heat exchange temperature regulation I-time |  | 1 | 1800 | s | 60
222 | Cool exchange temperature regulation P-band |  | 1.00 | 10.00 | K | 6.00 | 1.11
223 | Cool exchange temperature regulation I-time |  | 1 | 1800 | s | 50 | 1.11
AHU Heat/Cool
226 | Re-heat P-band |  | 1.00 | 40.00 | K | 8.00
227 | Re-heat I-time |  | 1 | 1800 | s | 70
230 | Re-heat periodic operation interval |  | 0 | 168 | h | 24
231 | Re-heat periodic operation time |  | 0 | 60 | min | 3
239 | Extra regulation sequence 1 heat max output signal | Maximum output signal setting for the extra regulation sequence. | 0.00 | 100.00 | % | 100.00
240 | Extra regulation sequence 1 cool max output signal | Maximum output signal setting for the extra regulation sequence. | 0.00 | 100.00 | % | 100.00
241 | Extra regulation sequence 1 heat P-band |  | 1.00 | 40.00 | K | 8
242 | Extra regulation sequence 1 heat I-time |  | 1 | 1800 | s | 70
243 | Extra regulation sequence 1 cool P-band |  | 1.00 | 40.00 | K | 9
244 | Extra regulation sequence 1 cool I-time |  | 1 | 1800 | s | 80
247 | Extra regulation 1 periodic operation interval |  | 0 | 168 | h | 24
248 | Extra regulation 1 periodic operation time |  | 0 | 60 | min | 3
252 | Extra regulation 1 temperature protection temperature |  | -50.00 | 100.00 | °C | 0.00
253 | Extra regulation 1 temperature protection alarm delay |  | 0 | 9999 | min | 5
258 | Cool step 1 min supply air flow limit |  | 0 | AV 259 | l/s |  | 1.16
259 | Cool step 2 min supply air flow limit |  | AV 258 | AV 260 | l/s |  | 1.16
260 | Cool step 3 min supply air flow limit |  | AV 259 | AI 57 | l/s |  | 1.16
262 | Cool SA neutral zone |  | 0.50 | 10.00 | K | 0.50
263 | Cool EA neutral zone |  | 0.50 | 10.00 | K | 0.50
264 | Cool outdoor temp limit 1 |  | 0.00 | 30.00 | °C | 15.00
265 | Cool outdoor temp limit 2 |  | 0.00 | 30.00 | °C | 18.00
266 | Cool outdoor temp limit 3 |  | 0.00 | 30.00 | °C | 20.00
267 | Cool 0-10V min supply air flow limit |  | 0 | AI 57 | l/s
268 | Cool 0-10V min extract air flow limit |  | 0 | AI 58 | l/s
269 | Cool restart time | Setting of cool restart time between start-start. | 0 | 15 | min | 5
270 | Cool step up delay time | Setting of on/off cooling and COOL DX time delay between steps. | 0 | 10 | min | 5
271 | Cool stand still time | Setting of on/off cooling and COOL DX time delay before stop-start | 0 | 20 | min | 5
272 | Cool P-band |  | 1.00 | 40.00 | K | 9
273 | Cool I-time |  | 1 | 1800 | s | 80
277 | Cool periodic operation interval |  | 0 | 168 | h | 24
278 | Cool periodic operation time |  | 0 | 60 | min | 3
279 | Cool step 1 min extract air flow limit |  | 0 | AV 280 | l/s |  | 1.16
280 | Cool step 2 min extract air flow limit |  | AV 279 | AV 281 | l/s |  | 1.16
281 | Cool step 3 min extract air flow limit |  | AV 280 | AI 58 | l/s |  | 1.16
Summer night cool/Intermittent night heat /Morning boost
285 | Summer night cool start time (hour) |  | 0 | 23 | h | 23
286 | Summer night cool start time (minute) |  | 0 | 59 | min | 0
287 | Summer night cool stop time (hour) |  | 0 | 23 | h | 23
288 | Summer night cool stop time (minute) |  | 0 | 59 | min | 0
289 | Summer night cool OA temp start limit |  | -5.00 | 15.00 | °C | 10.00
290 | Summer night cool EA temp start limit |  | 17.00 | 27.00 | °C | 22.00
291 | Summer night cool EA temp stop limit |  | 12.00 | 22.00 | °C | 16.00
292 | Summer night cool SA temp set point |  | 0.00 | 20.00 | °C | 10.00
293 | Summer night cool SA flow set point |  | AI 55 | AI 57 | l/s |  | 1.22
294 | Summer night cool EA flow set point |  | AI 56 | AI 58 | l/s |  | 1.22
297 | Intermittent night heat SA flow set point |  | AI 55 | AI 57 | l/s
298 | Intermittent night heat SA duct pressure set point |  | 20 | 750 | Pa | 100
299 | Intermittent night heat EA temp start limit |  | 5.00 | AV 300 | °C | 16.00
300 | Intermittent night heat EA temp stop limit |  | AV 299 | 25.00 | °C | 18.00
301 | Intermittent night heat SA temp set point |  | 5.00 | 50.00 | °C | 28.00
303 | Intermittent night heat EA flow set point |  | AI 56 | AI 58 | l/s |  | 1.12
304 | Intermittent night heat EA duct pressure set point |  | 20 | 750 | Pa |  | 1.12
306 | Morning boost start time (hour) |  | 0 | 23 | h | 0
307 | Morning boost start time (minute) |  | 0 | 59 | min | 0
308 | Morning boost air flow set point |  | AI 55 | AI 57 | l/s
309 | Morning boost duct pressure set point |  | 20 | 750 | Pa | 100
311 | Summer night cool SA duct pressure set point |  | 20 | 750 | Pa | 100 | 1.22
312 | Summer night cool EA duct pressure set point |  | 20 | 750 | Pa | 100 | 1.22
Cooling boost/heating boost
314 | Cooling boost comfort start limit |  | 2.00 | 10.00 | K | 3.00
315 | Cooling boost comfort regulation speed |  | 0.01 | 25 | %/s | 4
316 | Cooling boost economy P-band |  | 1 | 40.00 | K | 5.00
317 | Cooling boost economy I-time |  | 1 | 1800 | s | 50
321 | Heating boost comfort start limit |  | 2.00 | 10.00 | K | 3.00
322 | Heating boost comfort regulation speed |  | 0.01 | 25 | %/s | 4
Xzone ERS-1 reg.
331 | Xzone ERS 1 step | Curve setting according to the diagram for ERS 1. | 1 | 4 |  | 2
332 | Xzone ERS 1 diff | Supply air temp differental setting according to the diagram for ERS 1. | 1 | 7.00 | K | 2.00
333 | Xzone ERS 1 breakpoint | Breakpoint temp setting according to the diagram for ERS 1. | 12.00 | 26.00 | °C | 22.00
Xzone ERS-2 reg.
336 | Xzone ERS 2 breakpoint X1 | Breakpoint X1 setting according to the diagram for ERS 2. | 10 | AV 337 | °C | 15.00
337 | Xzone ERS 2 breakpoint X2 | Breakpoint X2 setting according to the diagram for ERS 2. | AV 336 | AV 338 | °C | 20.00
338 | Xzone ERS 2 breakpoint X3 | Breakpoint X3 setting according to the diagram for ERS 2. | AV 337 | AV 339 | °C | 22.00
339 | Xzone ERS 2 breakpoint X4 | Breakpoint X4 setting according to the diagram for ERS 2. | AV 338 | 40.00 | °C | 24.00
340 | Xzone ERS 2 breakpoint Y1 | Breakpoint Y1 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 20.00
341 | Xzone ERS 2 breakpoint Y2 | Breakpoint Y2 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 18.00
342 | Xzone ERS 2 breakpoint Y3 | Breakpoint Y3 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 14.00
343 | Xzone ERS 2 breakpoint Y4 | Breakpoint Y4 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 12.00
Xzone SA Reg.
346 | Xzone SA temperature set point | Supply air temperature setting, for supply air temp regulation mode. | 10.00 | 40.00 | °C | 21.00
Xzone EA Reg.
349 | Xzone EA/Room temperature set point | Extract air/room temperature setting, for Extract air/room temp regulation mode. | 10.00 | 40.00 | °C | 21.00
350 | Xzone SA min temp set point | Supply air min. set point during EA/room regulation mode. | 8.00 | 20.00 | °C | 16.00
351 | Xzone SA max temp set point | Supply air max. set point during EA/room regulation mode. | 16.00 | 50.00 | °C | 28.00
352 | Xzone EA regultaion P-band |  | 1.00 | 10.00 | K | 5.00
353 | Xzone EA regultaion I-time |  | 1 | 1800 | s | 180
Xzone ORS Reg.
354 | Xzone ORS breakpoint X1 | Breakpoint X1 setting according to the diagram for ORS. | -5.00 | AV 355 | °C | -20.00
355 | Xzone ORS breakpoint X2 | Breakpoint X2 setting according to the diagram for ORS. | AV 354 | AV 356 | °C | -10.00
356 | Xzone ORS breakpoint X3 | Breakpoint X3 setting according to the diagram for ORS. | AV 355 | AV 357 | °C | 10.00
357 | Xzone ORS breakpoint X4 | Breakpoint X4 setting according to the diagram for ORS. | AV 356 | 50.00 | °C | 20.00
358 | Xzone ORS breakpoint Y1 | Breakpoint Y1 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
359 | Xzone ORS breakpoint Y2 | Breakpoint Y2 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
360 | Xzone ORS breakpoint Y3 | Breakpoint Y3 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
361 | Xzone ORS breakpoint Y4 | Breakpoint Y4 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
Xzone ORE Reg.
364 | Xzone ORE breakpoint X1 | Breakpoint X1 setting according to the diagram for ORE. | -5.00 | AV 365 | °C | -20.00
365 | Xzone ORE breakpoint X2 | Breakpoint X2 setting according to the diagram for ORE. | AV 364 | AV 366 | °C | -10.00
366 | Xzone ORE breakpoint X3 | Breakpoint X3 setting according to the diagram for ORE. | AV 365 | AV 367 | °C | 10.00
367 | Xzone ORE breakpoint X4 | Breakpoint X4 setting according to the diagram for ORE. | AV 366 | 50.00 | °C | 20.00
368 | Xzone ORE breakpoint Y1 | Breakpoint Y1 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
369 | Xzone ORE breakpoint Y2 | Breakpoint Y2 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
370 | Xzone ORE breakpoint Y3 | Breakpoint Y3 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
371 | Xzone ORE breakpoint Y4 |  | 10.00 | 40.00 | °C | 21.50
Xzone external sensors
380 | Xzone external room temp from BMS |  | -55.00 | 125.00 | °C | 0.00
381 | Xzone external room temp from BMS alarm time |  | 0 | 9999 | min | 5
Xzone Heat/Cool
384 | Xzone reheat P-band |  | 1.00 | 40.00 | K | 8.00
385 | Xzone reheat I-time |  | 1 | 1800 | s | 70
388 | Xzone reheat periodic operation interval |  | 0 | 168 | h | 24
389 | Xzone reheat periodic operation time |  | 0 | 60 | min | 3
396 | Xzone Cool SA neutral zone |  | 0.50 | 10.00 | K | 0.50
397 | Xzone Cool EA neutral zone |  | 0.50 | 10.00 | K | 0.50
398 | Xzone Cool P-band |  | 1.00 | 40.00 | K | 6.00
399 | Xzone Cool I-time |  | 1 | 1800 | s | 60
403 | Xzone Cool periodic operation interval |  | 0 | 168 | h | 24
404 | Xzone Cool periodic operation time |  | 0 | 60 | min | 3
Pre-heat
411 | Pre-heat temperature set point |  | -40.00 | 40.00 | °C | 5.00
412 | Pre-heat P-band |  | 1.00 | 40.00 | K | 8.00
413 | Pre-heat I-time |  | 1 | 1800 | s | 70
416 | Pre-heat periodic operation interval |  | 0 | 168 | h | 24
417 | Pre-heat periodic operation time |  | 0 | 60 | min | 3
ReCO2
426 | ReCO2-CO2 set point |  | 0.00 | 100.00 | % | 50.00
427 | ReCO2 min. outdoor air |  | 0 | AI 57 | l/s
428 | ReCO2 min. exhaust air |  | 0 | AI 58 | l/s
429 | ReCO2-CO2 P-band |  | 1.00 | 100.00 | % | 50.00
430 | ReCO2-CO2 I-time |  | 1 | 1800 | s | 60
431 | ReCO2-CO2 air flow boost reg. P-band |  | 10.00 | 100.00 | % | 50.00
432 | ReCO2-CO2 air flow boost reg. I-time |  | 1 | 1800 | s | 60
433 | ReCO2 heat P-band |  | 1.00 | 40.00 | K | 5.00
434 | ReCO2 heat I-time |  | 1 | 1800 | s | 70
435 | ReCO2 cool P-band |  | 1.00 | 40.00 | K | 6.00
436 | ReCO2 cool I-time |  | 1 | 1800 | s | 60
437 | ReCO2-CO2 ppm set point |  | 0 | 10000 | ppm | 1000 | 1.28
438 | ReCO2-CO2 ppm P-band |  | 100 | 10000 | ppm | 600 | 1.28
439 | ReCO2-VOC ppm set point |  | 0 | 10000 | ppm | 1500 | 1.28
440 | ReCO2-VOC ppm P-band |  | 100 | 10000 | ppm | 1000 | 1.28
Humidity/VOC
443 | Humidifying on/off start level |  | 10.00 | AV 444 | %RH | 40.00
444 | Humidifying on/off stop level |  | AV 443 | 95.00 | %RH | 45.00
448 | Humidifying 0-10V set point |  | 10.00 | 95.00 | %RH | 30.00
449 | Humidifying 0-10V SA max set point |  | 10.00 | 95.00 | %RH | 80.00
450 | Humidifying 0-10V SA P-band |  | 1.00 | 200.00 | %RH | 60.00
451 | Humidifying 0-10V SA I-time |  | 1 | 1800 | s | 30
452 | Humidifying 0-10V EA P-band |  | 1.00 | 200.00 | %RH | 60.00
453 | Humidifying 0-10V EA I-time |  | 1 | 1800 | s | 180
458 | Dehumidifying SA set point |  | 10.00 | 90.00 | %RH | 50.00
460 | Dehumidifying EA set point |  | 10.00 | 90.00 | %RH | 50.00 | 1.18
COOL DX
470 | COOL DX Low pressure stop limit |  | 1.00 | 10.00 | Bar | 3.00
471 | COOL DX High pressure stop limit |  | 25.00 | 40.00 | Bar | 39.00
472 | COOL DX Restart time | Time setting between start - start | 5 | 15 | min | 5
SMART Link
482 | SMART Link WB Heat temperature set point |  | AI 299 | AI 300 | °C | 40.0
483 | SMART Link WB Heat temperature heat zone |  | 1.0 | 10.0 | K | 3.0
484 | SMART Link WB Cool temperature set point |  | AI 301 | AI 302 | °C | 12.0
485 | SMART Link WB Cool temperature heat zone |  | 1.0 | 10.0 | K | 2.0
491 | SMART Link WB Optimize valve upper limit |  | 5.0 | 90.0 | % | 80.0
492 | SMART Link WB Optimize valve lower limit |  | 70.0 | 100.0 | % | 100.0
493 | SMART Link WB Optimize time delay |  | 30 | 32000 | s | 60
494 | SMART Link WB Optimize heat regulation speed |  | 0.10 | 6.00 | K/s | 0.30
495 | SMART Link WB Optimize cool regulation speed |  | 0.10 | 6.00 | K/s | 0.30
510 | SMART Link DX Amount of units |  | 0 | 4 |  | 1
519 | SMART Link OA temp limit |  | -50.00 | 50.00 | °C | -30.00 | 1.12
AYC
524 | AYC Heated water temp set point |  | 10.00 | 80.00 | °C | 30.00
526 | AYC Heated water OA temp for start of pump |  | -40.00 | 40.00 | °C | 15.00
527 | AYC Heated water OA temp for stop of pump |  | -40.00 | 40.00 | °C | 18.00
532 | AYC Heated water periodic operation interval |  | 0 | 168 | h | 24
533 | AYC Heated water periodic operation time |  | 0 | 60 | min | 3
537 | AYC Heated water OA temp compensation X1 |  | -40.00 | AV 538 | °C | -20.00
538 | AYC Heated water OA temp compensation X2 |  | AV 537 | AV 539 | °C | 0.00
539 | AYC Heated water OA temp compensation X3 |  | AV 538 | AV 540 | °C | 5.00
540 | AYC Heated water OA temp compensation X4 |  | AV 539 | 40.00 | °C | 15.00
541 | AYC Heated water OA temp compensation Y1 |  | 10.00 | 80.00 | °C | 40.00
542 | AYC Heated water OA temp compensation Y2 |  | 10.00 | 80.00 | °C | 30.00
543 | AYC Heated water OA temp compensation Y3 |  | 10.00 | 80.00 | °C | 20.00
544 | AYC Heated water OA temp compensation Y4 |  | 10.00 | 80.00 | °C | 15.00
549 | AYC Heated water room temp compensation temperature |  | 0.00 | 40.00 | °C | 21.00
550 | AYC Heated water room temp compensation P-band |  | 1.00 | 10.00 | K | 5.00
554 | AYC Heated water night temp compensation temp |  | -10.00 | 10.00 | K | -2.00
556 | AYC Heated water night temp compensation start time 1 (hour) |  | 0 | 23 | h | 0
557 | AYC Heated water night temp compensation start time 1 (minutes) |  | 0 | 59 | min | 0
558 | AYC Heated water night temp compensation stop time 1 (hour) |  | 0 | 23 | h | 0
559 | AYC Heated water night temp compensation stop time 1 (minutes) |  | 0 | 59 | min | 0
563 | AYC Heated water night temp compensation start time 2 (hour) |  | 0 | 23 | h | 0
564 | AYC Heated water night temp compensation start time 2 (minutes) |  | 0 | 59 | min | 0
565 | AYC Heated water night temp compensation stop time 2 (hour) |  | 0 | 23 | h | 0
566 | AYC Heated water night temp compensation stop time 2 (minutes) |  | 0 | 59 | min | 0
569 | AYC Heated water P-band |  | 1.00 | 40..00 | K | 15.00
570 | AYC Heated water I-time |  | 1 | 600 | s | 60
572 | AYC Chilled water temp set point |  | 10.00 | 80.00 | °C | 30.00
575 | AYC Chilled water OA temp for start of pump |  | -40.00 | 40.00 | °C | 15.00
576 | AYC Chilled water OA temp for stop of pump |  | -40.00 | 40.00 | °C | 18.00
581 | AYC Chilled water periodic operation interval |  | 0 | 168 | h | 24
582 | AYC Chilled water periodic operation time |  | 0 | 60 | min | 3
586 | AYC Chilled water OA temp compensation X1 |  | -40.00 | AV 587 | °C | -20.00
587 | AYC Chilled water OA temp compensation X2 |  | AV 586 | AV 588 | °C | 0.00
588 | AYC Chilled water OA temp compensation X3 |  | AV 587 | AV 589 | °C | 5.00
589 | AYC Chilled water OA temp compensation X4 |  | AV 588 | 40.00 | °C | 15.00
590 | AYC Chilled water OA temp compensation Y1 |  | 5.00 | 30.00 | °C | 22.00
591 | AYC Chilled water OA temp compensation Y2 |  | 5.00 | 30.00 | °C | 18.00
592 | AYC Chilled water OA temp compensation Y3 |  | 5.00 | 30.00 | °C | 14.00
593 | AYC Chilled water OA temp compensation Y4 |  | 5.00 | 30.00 | °C | 12.00
598 | AYC Chilledwater room temp compensation temperature |  | 0.00 | 40.00 | °C | 21.00
599 | AYC Chilled water room temp compensation P-band |  | 1.00 | 10.00 | K | 5.00
603 | AYC Chilled water night temp compensation temp |  | -10.00 | 10.00 | K | -2.00
605 | AYC Chilled water night temp compensation start time 1 (hour) |  | 0 | 23 | h | 0
606 | AYC Chilled water night temp compensation start time 1 (minutes) |  | 0 | 59 | min | 0
607 | AYC Chilled water night temp compensation stop time 1 (hour) |  | 0 | 23 | h | 0
608 | AYC Chilled water night temp compensation stop time 1 (minutes) |  | 0 | 59 | min | 0
612 | AYC Chilled water night temp compensation start time 2 (hour) |  | 0 | 23 | h | 0
613 | AYC Chilled water night temp compensation start time 2 (minutes) |  | 0 | 59 | min | 0
614 | AYC Chilledwater night temp compensation stop time 2 (hour) |  | 0 | 23 | h | 0
615 | AYC Chilled water night temp compensation stop time 2 (minutes) |  | 0 | 59 | min | 0
619 | AYC Chilled water dew point compensation neutral zone |  | 0 | 5.00 | K | 2.00
620 | AYC Chilled water dew point compensation regulation speed | Percent air flow boost of each increased chilled water set point. | 0 | 30.00 | %/K | 10.00
623 | AYC Chilled water P-band |  | 1.00 | 40..00 | K | 15.00
624 | AYC Chilled water I-time |  | 1 | 600 | s | 60
Optimize
638 | Optimize SA pressure set point |  | 20.0 | 750.0 | Pa | 0
639 | Optimize EA pressure set point |  | 20.0 | 750.0 | Pa | 0
MIRU Control
672 | MIRU Control 1 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
673 | MIRU Control 1 High speed duct pressure set point |  | 0 | 750 | Pa | 200
674 | MIRU Control 1 Low speed air flow set point |  | AI 400 | AI 401 | l/s
675 | MIRU Control 1 High speed air flow set point |  | AI 400 | AI 401 | l/s
680 | MIRU Control 2 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
681 | MIRU Control 2 High speed duct pressure set point |  | 0 | 750 | Pa | 200
682 | MIRU Control 2 Low speed air flow set point |  | AI 417 | AI 418 | l/s
683 | MIRU Control 2 High speed air flow set point |  | AI 417 | AI 418 | l/s
688 | MIRU Control 3 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
689 | MIRU Control 3 High speed duct pressure set point |  | 0 | 750 | Pa | 200
690 | MIRU Control 3 Low speed air flow set point |  | AI 434 | AI 435 | l/s
691 | MIRU Control 3 High speed air flow set point |  | AI 434 | AI 435 | l/s
696 | MIRU Control 4 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
697 | MIRU Control 4 High speed duct pressure set point |  | 0 | 750 | Pa | 200
698 | MIRU Control 4 Low speed air flow set point |  | AI 451 | AI 452 | l/s
699 | MIRU Control 4 High speed air flow set point |  | AI 451 | AI 452 | l/s
704 | MIRU Control 5 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
705 | MIRU Control 5 High speed duct pressure set point |  | 0 | 750 | Pa | 200
706 | MIRU Control 5 Low speed air flow set point |  | AI 468 | AI 469 | l/s
707 | MIRU Control 5 High speed air flow set point |  | AI 468 | AI 469 | l/s
712 | MIRU Control 6 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
713 | MIRU Control 6 High speed duct pressure set point |  | 0 | 750 | Pa | 200
714 | MIRU Control 6 Low speed air flow set point |  | AI 485 | AI 486 | l/s
715 | MIRU Control 6 High speed air flow set point |  | AI 485 | AI 486 | l/s
720 | MIRU Control 7 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
721 | MIRU Control 7 High speed duct pressure set point |  | 0 | 750 | Pa | 200
722 | MIRU Control 7 Low speed air flow set point |  | AI 502 | AI 503 | l/s
723 | MIRU Control 7 High speed air flow set point |  | AI 502 | AI 503 | l/s
728 | MIRU Control 8 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
729 | MIRU Control 8 High speed duct pressure set point |  | 0 | 750 | Pa | 200
730 | MIRU Control 8 Low speed air flow set point |  | AI 519 | AI 520 | l/s
731 | MIRU Control 8 High speed air flow set point |  | AI 519 | AI 520 | l/s
736 | MIRU Control 9 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
737 | MIRU Control 9 High speed duct pressure set point |  | 0 | 750 | Pa | 200
738 | MIRU Control 9 Low speed air flow set point |  | AI 536 | AI 537 | l/s
739 | MIRU Control 9 High speed air flow set point |  | AI 536 | AI 537 | l/s
744 | MIRU Control 10 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
745 | MIRU Control 10 High speed duct pressure set point |  | 0 | 750 | Pa | 200
746 | MIRU Control 10 Low speed air flow set point |  | AI 553 | AI 554 | l/s
747 | MIRU Control 10 High speed air flow set point |  | AI 553 | AI 554 | l/s
Efficiency measurement
752 | Delta temperature alarm limit |  | 3.00 | 20.00 | K | 6.00 | 1.23
753 | Efficiency alarm limit |  | 10.00 | 70.00 | % | 50.00 | 1.23
Neutral zone
754 | Extra regulation sequence 1 heat neutral zone |  | 0 | 10.00 | K | 0 | 1.32
755 | Extra regulation sequence 2 heat neutral zone |  | 0 | 10.00 | K | 0 | 1.32
756 | ReCO2 heat neutral zone |  | 0 | 10.00 | K | 0 | 1.32
757 | H/C heat neutral zone |  | 0 | 10.00 | K | 0 | 1.32
758 | Re-heat neutral zone |  | 0 | 10.00 | K | 0 | 1.32
759 | Extra regulation sequence 1 cool neutral zone |  | 0 | 10.00 | K | 0 | 1.32
760 | Extra regulation sequence 2 cool neutral zone |  | 0 | 10.00 | K | 0 | 1.32
761 | ReCO2 cool neutral zone |  | 0 | 10.00 | K | 0 | 1.32
762 | H/C cool neutral zone |  | 0 | 10.00 | K | 0 | 1.32
763 | Cool neutral zone |  | 0 | 10.00 | K | 0 | 1.32
764 | Cooling boost neutral zone |  | 0 | 10.00 | K | 0 | 1.32
Night temp compensation
776 | Night temp compensation temp |  | -10.00 | 0 | K | -2.00 | 1.31
778 | Night temp compensation start time 1 (hour) |  | 0 | 23 | h | 0 | 1.31
779 | Night temp compensation start time 1 (minute) |  | 0 | 59 | min | 0 | 1.31
780 | Night temp compensation stop time 1 (hour) |  | 0 | 23 | h | 0 | 1.31
781 | Night temp compensation stop time 1 (minute) |  | 0 | 59 | min | 0 | 1.31
783 | Night temp compensation start time 2 (hour) |  | 0 | 23 | h | 0 | 1.31
784 | Night temp compensation start time 2 (minute) |  | 0 | 59 | min | 0 | 1.31
785 | Night temp compensation stop time 2 (hour) |  | 0 | 23 | h | 0 | 1.31
786 | Night temp compensation stop time 2 (minute) |  | 0 | 59 | min | 0 | 1.31
BMS I/O-modules
800 | External operation I/O-module A, analogue output |  | 0.00 | 100.00 | % | 0.00 | 1.20
801 | External operation I/O-module B, analogue output |  | 0.00 | 100.00 | % | 0.00 | 1.20
802 | External operation I/O-module C, analogue output |  | 0.00 | 100.00 | % | 0.00 | 1.20
Reserved
818 | Extra regulation sequence 2 heat max output signal | Maximum output signal setting for the extra regulation sequence. | 0.00 | 100.00 | % | 100.00 | 1.13
819 | Extra regulation sequence 2 cool max output signal | Maximum output signal setting for the extra regulation sequence. | 0.00 | 100.00 | % | 100.00 | 1.13
820 | Extra regulation sequence 2 heat P-band |  | 1.00 | 10.00 | K | 8 | 1.13
821 | Extra regulation sequence 2 heat I-time |  | 1 | 1800 | s | 70 | 1.13
822 | Extra regulation sequence 2 cool P-band |  | 1.00 | 10.00 | K | 6 | 1.13
823 | Extra regulation sequence 2 cool I-time |  | 1 | 1800 | s | 60 | 1.13
826 | Extra regulation 2 periodic operation interval |  | 0 | 168 | h | 24 | 1.13
827 | Extra regulation 2 periodic operation time |  | 0 | 60 | min | 3 | 1.13
830 | Seasonal controlled supply air |  | 0.00 | 40.00 | C | 21.00 | 1.28
831 | Seasonal controlled extract air/room temp |  | 0.00 | 40.00 | C | 21.00 | 1.28
832 | Seasonal controlled supply air min temp |  | 0.00 | 30.00 | C | 16.00 | 1.28
833 | Seasonal controlled supply air max temp |  | 8.00 | 50.00 | C | 28.00 | 1.28
H/C
852 | H/C outdoor temperature limit heating |  | -50.00 | 50.00 | °C | -20.00 | 1.23
853 | H/C outdoor temperature limit cooling |  | 0.00 | 50.00 | °C | 15.00 | 1.23
854 | H/C air flow limit supply air |  | 0 | AI 57 | l/s |  | 1.23
855 | H/C air flow limit extract air |  | 0 | AI 58 | l/s |  | 1.23
Humidity
891 | Humidifying start time 1 (hour) |  | 0 | 23 | h | 0 | 2.37
892 | Humidifying start time 1 (minute) |  | 0 | 59 | min | 0 | 2.37
893 | Humidifying stop time 1 (hour) |  | 0 | 23 | h | 0 | 2.37
894 | Humidifying stop time 1 (minute) |  | 0 | 59 | min | 0 | 2.37
896 | Humidifying start time 2 (hour) |  | 0 | 23 | h | 0 | 2.37
897 | Humidifying start time 2 (minute) |  | 0 | 59 | min | 0 | 2.37
898 | Humidifying stop time 2 (hour) |  | 0 | 23 | h | 0 | 2.37
899 | Humidifying stop time 2 (minute) |  | 0 | 59 | min | 0 | 2.37
901 | Humidifying start time 3 (hour) |  | 0 | 23 | h | 0 | 2.37
902 | Humidifying start time 3 (minute) |  | 0 | 59 | min | 0 | 2.37
903 | Humidifying stop time 3 (hour) |  | 0 | 23 | h | 0 | 2.37
904 | Humidifying stop time 3 (minute) |  | 0 | 59 | min | 0 | 2.37
906 | Humidifying start time 4 (hour) |  | 0 | 23 | h | 0 | 2.37
907 | Humidifying start time 4 (minute) |  | 0 | 59 | min | 0 | 2.37
908 | Humidifying stop time 4 (hour) |  | 0 | 23 | h | 0 | 2.37
909 | Humidifying stop time 4 (minute) |  | 0 | 59 | min | 0 | 2.37
910 | Humidifying start time | Humidifying time channel start level | 10.00 | AV 911 | %RH | 50.00 | 2.37
911 | Humidifying stop time | Humidifying time channel stop level | AV 910 | 95.00 | %RH | 55.00 | 2.37
912 | Humidifying time | Humidifying time channel set point | 10.00 | 95.00 | %RH | 40.00 | 2.37
Time schedule
1268 | Prolonged low speed hours | Setting for prolonged external low speed operation. | 0 | 23 |  | 0 | 1.13
1269 | Prolonged low speed minutes | Setting for prolonged external low speed operation. | 0 | 59 |  | 0 | 1.13
1270 | Prolonged high speed hours | Setting for prolonged external high speed operation. | 0 | 23 |  | 0 | 1.13
1271 | Prolonged high speed minutes | Setting for prolonged external high speed operation. | 0 | 59 |  | 0 | 1.13
External override
3000 | External override code 1 |  | 0 | 9999 |  | 0 | 1.30
3001 | External override code 2 |  | 0 | 9999 |  | 0 | 1.30
3002 | External override, duration |  | 1 | 72 | h | 1 | 1.30
3010 | External override value, Supply air fan level |  | 0 | 100.00 | % | 0 | 1.30
3011 | External override value, Extract air fan level |  | 0 | 100.00 | % | 0 | 1.30
3020 | External override value, RX HX level |  | 0 | 100.00 | % | 0 | 1.30
3030 | External override value, PX HX damper 3A |  | 0 | 100.00 | % | 0 | 1.30
3031 | External override value, PX HX damper 1A |  | 0 | 100.00 | % | 0 | 1.30
3032 | External override value, PX HX bypass 2A |  | 0 | 100.00 | % | 0 | 1.30
3040 | External override value, CX HX valve |  | 0 | 100.00 | % | 0 | 1.30
3041 | External override value, CX HX pump level |  | 0 | 100.00 | % | 0 | 1.30
3050 | External override value, Pre-heat level |  | 0 | 100.00 | % | 0 | 1.30
3060 | External override value, Reheat level |  | 0 | 100.00 | % | 0 | 1.30
3070 | External override value, Xzone heat level |  | 0 | 100.00 | % | 0 | 1.30
3080 | External override value, Extra reg. 1 level |  | 0 | 100.00 | % | 0 | 1.30
3090 | External override value, Extra reg. 2 level |  | 0 | 100.00 | % | 0 | 1.30
3100 | External override value, Cool level |  | 0 | 100.00 | % | 0 | 1.30
3110 | External override value, Xzone cool level |  | 0 | 100.00 | % | 0 | 1.30
3130 | External override value, HC comp. level |  | 0 | 100.00 | % | 0 | 1.30
3131 | External override value, HC defrost recirc. level |  | 0 | 100.00 | % | 0 | 1.30
3132 | External override value, HC defrost el. heat level |  | 0 | 100.00 | % | 0 | 1.30
3150 | External override value, SMART Link DX 1 comp. level |  | 0 | 100.00 | % | 0 | 1.30
3151 | External override value, SMART Link DX 2 comp. level |  | 0 | 100.00 | % | 0 | 1.30
3152 | External override value, SMART Link DX 3 comp. level |  | 0 | 100.00 | % | 0 | 1.30
3153 | External override value, SMART Link DX 4 comp. level |  | 0 | 100.00 | % | 0 | 1.30
3170 | External override value, Humidifying level |  | 0 | 100.00 | % | 0 | 1.30
3180 | External override value, ReCO2 recirculation damper |  | 0 | 100.00 | % | 0 | 1.30
3181 | External override value, ReCO2 outdoor damper |  | 0 | 100.00 | % | 0 | 1.30
3190 | External override value, AYC heat valve level |  | 0 | 100.00 | % | 0 | 1.30
3191 | External override value, AYC cool valve level |  | 0 | 100.00 | % | 0 | 1.30
3220 | External override value, Miru 1 fan level |  | 0 | 100.00 | % | 0 | 1.30
3221 | External override value, Miru 2 fan level |  | 0 | 100.00 | % | 0 | 1.30
3222 | External override value, Miru 3 fan level |  | 0 | 100.00 | % | 0 | 1.30

## Binary Input
GOLD_E_F_BACnet_230307
Binary Input (RO).
Object Instance | Object Name | Description | Min | Max | Unit | Default | Misc
Operation level/alarm
1 | Operation active | Relay output status | 0 | 1
2 | Damper operation active | Relay output status | 0 | 1
3 | Low speed operation active | Low speed operation status | 0 | 1
4 | High speed operation active | High speed operation status | 0 | 1
5 | Intermittent night heat active |  | 0 | 1
6 | Morning boost active |  | 0 | 1
7 | Heating boost active |  | 0 | 1
8 | Cooling boost active |  | 0 | 1
9 | Summer night cool active |  | 0 | 1
13 | A-alarm active | Any alarm with priority class A active | 0 | 1
14 | B-alarm active | Any alarm with priority class B active | 0 | 1
Heat exchange
17 | HX operation active | HX status | 0 | 1
18 | HX cool recovery active | HX cool recovery status | 0 | 1
19 | HX defrost active | HX defrost status | 0 | 1
22 | RHX speed monitor signal | RHX speed monitor status | 0 | 1
27 | CHX pump output | CHX-1 relay output status | 0 | 1
28 | CHX pump input | CHX-1 digital input status | 0 | 1
AHU Coils
31 | Season heat, extra regulation sequence allowed |  | 0 | 1
32 | Season heat, re-heat allowed |  | 0 | 1
33 | Extra regulation sequence 1, output | Relay output status | 0 | 1
34 | Extra regulation sequence 1, power reduction active |  | 0 | 1
35 | Extra regulation sequence 1, anti-frost regulation active |  | 0 | 1
36 | Extra regulation sequence 1 combi coil input |  | 0 | 1 |  |  | 2.37
37 | Extra regulation sequence 1 combi coil output |  | 0 | 1 |  |  | 2.37
38 | Re-heat output | Relay output status | 0 | 1
39 | Re-heat power reduction active |  | 0 | 1
40 | Re-heat anti-frost regulation active |  | 0 | 1
43 | Cool output 1 | Relay output status | 0 | 1
44 | Cool output 2 | Relay output status | 0 | 1
46 | Extra regulation sequence 2 combi coil input |  | 0 | 1 |  |  | 2.37
47 | Extra regulation sequence 2 combi coil output |  | 0 | 1 |  |  | 2.37
48 | Extra regulation sequence 2, output | Relay output status | 0 | 1 |  |  | 1.13
49 | Extra regulation sequence 2, power reduction active |  | 0 | 1 |  |  | 1.13
50 | Extra regulation sequence 2, anti-frost regulation active |  | 0 | 1 |  |  | 1.13
Pre-heat
51 | Pre-heat output | Relay output status | 0 | 1
52 | Pre-heat power reduction active |  | 0 | 1
53 | Pre-heat anti-frost regulation active |  | 0 | 1
Xzone
56 | Xzone heat output | Relay output status | 0 | 1
57 | Xzone heat power reduction active |  | 0 | 1
58 | Xzone heat anti-frost regulation active |  | 0 | 1
63 | Xzone cool output 1 | Relay output status | 0 | 1
64 | Xzone cool output 2 | Relay output status | 0 | 1
AYC
99 | AYC heat pump output | Relay output status | 0 | 1
100 | AYC heat pump input | Digital input status | 0 | 1
104 | Max. limit for the supply air fan speed when running in pressure regulation mode. | Relay output status | 0 | 1
105 | AYC cool pump input | Digital input status | 0 | 1
COOL DX
109 | COOL DX compressor 1 output | Relay output status | 0 | 1
110 | COOL DX compressor 1 input | Digital input status | 0 | 1
115 | COOL DX compressor 2 output | Relay output status | 0 | 1
116 | COOL DX compressor 2 input | Digital input status | 0 | 1
BMS I/O-modules
200 | External operation I/O-module 3, digital input 1 |  | 0 | 1 |  |  | 1.20
201 | External operation I/O-module 3, digital input 2 |  | 0 | 1 |  |  | 1.20
202 | External operation I/O-module 3, digital output 1 |  | 0 | 1 |  |  | 1.20
203 | External operation I/O-module 3, digital output 2 |  | 0 | 1 |  |  | 1.20
204 | External operation I/O-module 6, digital input 1 |  | 0 | 1 |  |  | 1.20
205 | External operation I/O-module 6, digital input 2 |  | 0 | 1 |  |  | 1.20
206 | External operation I/O-module 6, digital output 1 |  | 0 | 1 |  |  | 1.20
207 | External operation I/O-module 6, digital output 2 |  | 0 | 1 |  |  | 1.20
208 | External operation I/O-module A, digital input |  | 0 | 1 |  |  | 1.20
209 | External operation I/O-module B, digital input |  | 0 | 1 |  |  | 1.20
210 | External operation I/O-module C, digital input |  | 0 | 1 |  |  | 1.20
SMART Link
319 | SMART Link, DX operation |  | 0 | 1
323 | SMART Link, DX unit 1 operation |  | 0 | 1
324 | SMART Link, DX unit 1 cool mode |  | 0 | 1
325 | SMART Link, DX unit 1 defrost request |  | 0 | 1
326 | SMART Link, DX unit 1 defrost active |  | 0 | 1
334 | SMART Link, DX unit 2 operation |  | 0 | 1
335 | SMART Link, DX unit 2 cool mode |  | 0 | 1
336 | SMART Link, DX unit 2 defrost request |  | 0 | 1
337 | SMART Link, DX unit 2 defrost active |  | 0 | 1
345 | SMART Link, DX unit 3 operation |  | 0 | 1
346 | SMART Link, DX unit 3 cool mode |  | 0 | 1
347 | SMART Link, DX unit 3 defrost request |  | 0 | 1
348 | SMART Link, DX unit 3 defrost active |  | 0 | 1
356 | SMART Link, DX unit 4 operation |  | 0 | 1
357 | SMART Link, DX unit 4 cool mode |  | 0 | 1
358 | SMART Link, DX unit 4 defrost request |  | 0 | 1
359 | SMART Link, DX unit 4 defrost active |  | 0 | 1
367 | SMART Link, DX Defrost airflow increase status |  | 0 | 1 |  |  | 1.26
Alarms
501 | Alarm 1:1 External fire alarm no. 1 tripped |  | 0 | 1
502 | Alarm 1:2 External fire alarm no. 2 tripped |  | 0 | 1
503 | Alarm 1:3 Internal fire alarm tripped |  | 0 | 1
516 | Alarm 2:1 External alarm no. 1 tripped |  | 0 | 1
517 | Alarm 2:2 External alarm no. 2 tripped |  | 0 | 1
531 | Alarm 3:1 Pre-heat I/O-module no. 9 com. error |  | 0 | 1
532 | Alarm 3:2 Pre-heat electrical heater overheat protection tripped |  | 0 | 1
533 | Alarm 3:3 Pre-heat frost protection tripped |  | 0 | 1
534 | Alarm 3:4 Pre-heat frost protection temperature sensor defective |  | 0 | 1
535 | Alarm 3:5 Pre-heat temperature sensor defective |  | 0 | 1
536 | Alarm 3:6 Pre-heat valve monitoring tripped |  | 0 | 1
537 | Alarm 3:7 Pre-heat temperature below set point alarm limit |  | 0 | 1
538 | Alarm 3:8 Pre-heat alarm input tripped |  | 0 | 1
546 | Alarm 4:1 Extra reg. sequence 1 I/O-module no. E com. error |  | 0 | 1 |  |  | 1.13
547 | Alarm 4:2 Extra reg. sequence 1 electrical heater overheat protection tripped |  | 0 | 1 |  |  | 1.13
548 | Alarm 4:3 Extra reg. sequence 1 frost protection tripped |  | 0 | 1 |  |  | 1.13
549 | Alarm 4:4 Extra reg. sequence 1 frost protection temperature sensor defective |  | 0 | 1 |  |  | 1.13
550 | Alarm 4:5 Extra reg. sequence 1 valve monitoring tripped |  | 0 | 1 |  |  | 1.13
551 | Alarm 4:6 Extra reg. sequence 1 alarm input tripped |  | 0 | 1 |  |  | 1.13
552 | Alarm 4:7 Extra reg. sequence 1 temperature protection from com. Error |  | 0 | 1 |  |  | 1.13
553 | Alarm 4:8 Extra reg. sequence 1 combi coil temperature sensor defective |  | 0 | 1 |  |  | 1.26
554 | Alarm 4:9 Extra reg. sequence 2 I/O-module no. F com. error |  | 0 | 1 |  |  | 1.13
555 | Alarm 4:10 Extra reg. sequence 2 electrical heater overheat protection tripped |  | 0 | 1 |  |  | 1.13
556 | Alarm 4:11 Extra reg. sequence 2 frost protection tripped |  | 0 | 1 |  |  | 1.13
557 | Alarm 4:12 Extra reg. sequence 2 frost protection temperature sensor defective |  | 0 | 1 |  |  | 1.13
558 | Alarm 4:13 Extra reg. sequence 2 valve monitoring tripped |  | 0 | 1 |  |  | 1.13
559 | Alarm 4:14 Extra reg. sequence 2 alarm input tripped |  | 0 | 1 |  |  | 1.13
560 | Alarm 4:15 Extra reg. sequence 2 combi coil temperature sensor defective |  | 0 | 1 |  |  | 1.26
561 | Alarm 5:1 Re-heat electrical heater over heat protection tripped |  | 0 | 1
562 | Alarm 5:2 Re-heat frost protection tripped |  | 0 | 1
563 | Alarm 5:3 Re-heat frost protection temperature sensor defective |  | 0 | 1
564 | Alarm 5:4 Re-heat valve monitoring tripped |  | 0 | 1
565 | Alarm 5:5 Re-heat alarm input tripped |  | 0 | 1 |  |  | 1.27
576 | Alarm 6:1 Xzone I/O-module no. A com. error |  | 0 | 1
577 | Alarm 6:2 Xzone electrical heater overheat protection tripped |  | 0 | 1
578 | Alarm 6:3 Xzone frost protection tripped |  | 0 | 1
579 | Alarm 6:4 Xzone frost protection temperature sensor defective |  | 0 | 1
580 | Alarm 6:5 Xzone supply air temperature sensor defective |  | 0 | 1
581 | Alarm 6:6 Xzone heat valve monitoring tripped |  | 0 | 1
582 | Alarm 6:7 Xzone supply air temperature below set point alarm limit |  | 0 | 1
583 | Alarm 6:8 Xzone supply air temperature above set point alarm limit |  | 0 | 1
584 | Alarm 6:9 Xzone heat alarm input tripped |  | 0 | 1
591 | Alarm 7:1 Xzone I/O-module no. B com. error |  | 0 | 1
592 | Alarm 7:2 Xzone extract air temperature sensor defective |  | 0 | 1
593 | Alarm 7:3 Xzone cool valve monitoring tripped |  | 0 | 1
594 | Alarm 7:4 Xzone extract air temperature below set point alarm limit |  | 0 | 1
595 | Alarm 7:5 Xzone cool alarm input 1 tripped |  | 0 | 1
596 | Alarm 7:6 Xzone cool alarm input 2 tripped |  | 0 | 1
610 | Alarm 8:5 Cool valve monitoring tripped |  | 0 | 1
611 | Alarm 8:6 Cool alarm input 1 tripped |  | 0 | 1 |  |  | 1.27
612 | Alarm 8:7 Cool alarm input 2 tripped |  | 0 | 1 |  |  | 1.27
636 | Alarm 10:1 Supply air temperature sensor defective |  | 0 | 1
637 | Alarm 10:2 Supply air temperature sensor for density compensation defective |  | 0 | 1
638 | Alarm 10:3 Extract air temperature sensor defective |  | 0 | 1
639 | Alarm 10:4 Extract air temperature sensor for density compensation defective |  | 0 | 1
640 | Alarm 10:5 Extract air temperature sensor for heat exchanger defrosting def. |  | 0 | 1
641 | Alarm 10:6 Extract air temp. sensor for density compensation in SD AHU def. |  | 0 | 1
642 | Alarm 10:7 Extract air duct temperature sensor defective |  | 0 | 1 |  |  | 1.13
645 | Alarm 10:10 Outdoor air temperature sensor defective |  | 0 | 1
651 | Alarm 11:1 Room temperature sensor no. 1 defective |  | 0 | 1
652 | Alarm 11:2 Room temperature sensor no. 2 defective |  | 0 | 1
653 | Alarm 11:3 Room temperature sensor no. 3 defective |  | 0 | 1
654 | Alarm 11:4 Room temperature sensor no. 4 defective |  | 0 | 1
655 | Alarm 11:5 Xzone room temperature sensor no. 5 defective |  | 0 | 1
656 | Alarm 11:6 Xzone room temperature sensor no. 6 defective |  | 0 | 1
657 | Alarm 11:7 Xzone room temperature sensor no. 7 defective |  | 0 | 1
658 | Alarm 11:8 Xzone room temperature sensor no. 8 defective |  | 0 | 1
659 | Alarm 11:9 Outdoor temperature sensor no. A defective |  | 0 | 1
660 | Alarm 11:10 Outdoor temperature sensor no. B defective |  | 0 | 1
661 | Alarm 11:11 Outdoor temperature sensor no. C defective |  | 0 | 1
662 | Alarm 11:12 Outdoor temperature sensor no. D defective |  | 0 | 1
663 | Alarm 11:13 Room temperature from com. error |  | 0 | 1
664 | Alarm 11:14 Xzone room temperature from com. error |  | 0 | 1
665 | Alarm 11:15 Outdoor temperature from com. error |  | 0 | 1
666 | Alarm 12:1 Supply air temperature below set point alarm limit |  | 0 | 1
667 | Alarm 12:2 Supply air temperature above set point alarm limit |  | 0 | 1
671 | Alarm 12:6 Extract air temperature below alarm limit |  | 0 | 1
676 | Alarm 12:11 Temperature guard below alarm limit |  | 0 | 1
678 | Alarm 12:13 Heat exchange efficiency below alarm limit |  | 0 | 1 |  |  | 1.22
681 | Alarm 13:1 Humidification I/O-module no. 4 com. error |  | 0 | 1
682 | Alarm 13:2 Supply air humidity sensor defective |  | 0 | 1
683 | Alarm 13:3 Extract air humidity sensor defective |  | 0 | 1
684 | Alarm 13:4 Exhaust air humidity sensor defective |  | 0 | 1 |  |  | 1.22
685 | Alarm 13:5 Outdoor air humidity sensor defective |  | 0 | 1 |  |  | 2.36
686 | Alarm 13:6 Room humidity sensor defective |  | 0 | 1 |  |  | 2.36
689 | Alarm 13:9 Humidifier alarm output tripped |  | 0 | 1
691 | Alarm 13:11 VOC sensor com. error |  | 0 | 1
692 | Alarm 13:12 VOC sensor internal com. error |  | 0 | 1
693 | Alarm 13:13 VOC sensor internal error |  | 0 | 1
694 | Alarm 13:14 VOC sensor level below/above set point alarm limit |  | 0 | 1
711 | Alarm 15:1 Plate heat exchanger I/O-module no. 2 com. error |  | 0 | 1
712 | Alarm 15:2 Plate heat exchanger temperature sensor no. 1 defective |  | 0 | 1
713 | Alarm 15:3 Plate heat exchanger temperature sensor no. 2 defective |  | 0 | 1
714 | Alarm 15:4 Plate heat exchanger damper monitor tripped |  | 0 | 1
717 | Alarm 15:7 Plate heat exchanger I/O-module no. 3 com. error |  | 0 | 1 |  |  | 1.13
718 | Alarm 15:8 Plate heat exchanger bypass damper monitor tripped |  | 0 | 1 |  |  | 1.13
719 | Alarm 15:9 Plate heat exchanger damper no. 1 monitor tripped |  | 0 | 1 |  |  | 1.13
720 | Alarm 15:10 Plate heat exchanger damper no. 2 monitor tripped |  | 0 | 1 |  |  | 1.13
721 | Alarm 15:11 Plate heat exchanger I/O-module no. 3 com. error |  | 0 | 1 |  |  | 1.13
722 | Alarm 15:12 Plate heat exchanger bypass damper monitor tripped |  | 0 | 1 |  |  | 1.13
723 | Alarm 15:13 Plate counter flow heat exchanger defrost pressure above alarm limit |  | 0 | 1 |  |  | 1.22
724 | Alarm 15:14 Plate heat exchanger defrost pressure sensor no. C com. error |  | 0 | 1 |  |  | 1.13
725 | Alarm 15:15 Plate heat exchanger defrost pressure above alarm limit |  | 0 | 1 |  |  | 1.13
726 | Alarm 16:1 Coil heat exchanger I/O-module no. 1 com. error |  | 0 | 1
727 | Alarm 16:2 Coil heat exchanger temperature sensor defective |  | 0 | 1
728 | Alarm 16:3 Coil heat exchanger valve monitor tripped |  | 0 | 1
729 | Alarm 16:4 Coil heat exchanger pump monitor tripped |  | 0 | 1
730 | Alarm 16:5 Coil heat exchanger I/O-module no. C communication error |  | 0 | 1 |  |  | 1.20
731 | Alarm 16:6 Coil heat exchanger pressure sensor defective |  | 0 | 1 |  |  | 1.20
732 | Alarm 16:7 Coil heat exchanger low pressure brine circuit |  | 0 | 1 |  |  | 1.20
733 | Alarm 16:8 Coil heat exchanger pressure below alarm limit |  | 0 | 1 |  |  | 1.27
741 | Alarm 17:1 Rotary heat exchanger motor controller com. error |  | 0 | 1
742 | Alarm 17:2 Rotary heat exchanger defrost pressure sensor no. 7 com. error |  | 0 | 1
743 | Alarm 17:3 Rotary heat exchanger defrost pressure above alarm limit |  | 0 | 1
744 | Alarm 17:4 Rotary heat exchanger speed monitor tripped |  | 0 | 1
745 | Alarm 17:5 Rotary heat exchanger motor controller over current |  | 0 | 1
746 | Alarm 17:6 Rotary heat exchanger motor controller under voltage |  | 0 | 1
747 | Alarm 17:7 Rotary heat exchanger motor controller over voltage |  | 0 | 1
748 | Alarm 17:8 Rotary heat exchanger motor controller over temperature |  | 0 | 1
749 | Alarm 17:9 Rotary heat exchanger motor controller start error |  | 0 | 1
750 | Alarm 17:10 Rotary heat exchanger, motor controller internal error |  | 0 | 1 |  |  | 1.32
751 | Alarm 17:11 Rotary heat exchanger, motor controller phase error |  | 0 | 1 |  |  | 1.32
752 | Alarm 17:12 Rotary heat exchanger, motor controller internal memory error |  | 0 | 1 |  |  | 1.32
753 | Alarm 17:13 Rotary heat exchanger, motor controller current reduction |  | 0 | 1 |  |  | 1.32
754 | Alarm 17:14 Rotary heat exchanger, motor controller internal com. error |  | 0 | 1 |  |  | 1.32
755 | Alarm 17:15 Rotary heat exchanger, I/O-module com. error |  | 0 | 1 |  |  | 1.32
756 | Alarm 18:1 AYC I/O-module no. 7 com. error |  | 0 | 1
757 | Alarm 18:2 AYC heat temperature sensor defective |  | 0 | 1
758 | Alarm 18:3 AYC heat valve monitor tripped |  | 0 | 1
759 | Alarm 18:4 AYC heat pump monitor tripped |  | 0 | 1
760 | Alarm 18:5 AYC heat temperature below set point alarm limit |  | 0 | 1
761 | Alarm 18:6 AYC heat temperature above set point alarm limit |  | 0 | 1
764 | Alarm 18:9 AYC cool temperature sensor defective |  | 0 | 1
765 | Alarm 18:10 AYC cool valve monitor tripped |  | 0 | 1
766 | Alarm 18:11 AYC cool pump monitor tripped |  | 0 | 1
767 | Alarm 18:12 AYC cool temperature below set point alarm limit |  | 0 | 1
768 | Alarm 18:13 AYC cool temperature above set point alarm limit |  | 0 | 1
771 | Alarm 19:1 Rotary heat exchanger, AQC pressure sensor no. E com. error |  | 0 | 1 |  |  | 1.32
772 | Alarm 19:2 Rotary heat exchanger, AQC pressure below set point alarm limit |  | 0 | 1 |  |  | 1.32
773 | Alarm 19:3 Rotary heat exchanger, AQC damper monitoring tripped |  | 0 | 1 |  |  | 1.32
801 | Alarm 21:1 COOL DX I/O-module no. 2 com. error |  | 0 | 1
802 | Alarm 21:2 COOL DX compressor no. 1 low pressure sensor defective |  | 0 | 1
803 | Alarm 21:3 COOL DX compressor no. 1 low pressure below alarm limit |  | 0 | 1
804 | Alarm 21:4 COOL DX compressor no. 1 high pressure sensor defective |  | 0 | 1
805 | Alarm 21:5 COOL DX compressor no. 1 high pressure above alarm limit |  | 0 | 1
806 | Alarm 21:6 COOL DX compressor no. 1 monitor tripped |  | 0 | 1
807 | Alarm 21:7 COOL DX compressor no. 1 restart error |  | 0 | 1
808 | Alarm 21:8 COOL DX compressor no. 2 low pressure sensor defective |  | 0 | 1
809 | Alarm 21:9 COOL DX compressor no. 2 low pressure below alarm limit |  | 0 | 1
810 | Alarm 21:10 COOL DX compressor no. 2 high pressure sensor defective |  | 0 | 1
811 | Alarm 21:11 COOL DX compressor no. 2 high pressure above alarm limit |  | 0 | 1
812 | Alarm 21:12 COOL DX compressor no. 2 monitor tripped |  | 0 | 1
813 | Alarm 21:13 COOL DX compressor no. 2 restart error |  | 0 | 1
814 | Alarm 21:14 COOL DX outdoor air temperature sensor defective |  | 0 | 1
815 | Alarm 21:15 COOL DX phase sequence error or supply voltage missing |  | 0 | 1
831 | Alarm 23:1 SMART Link com. error |  | 0 | 1
832 | Alarm 23:2 SMART Link alarm level 1 tripped |  | 0 | 1
833 | Alarm 23:3 SMART Link alarm level 2 tripped |  | 0 | 1
834 | Alarm 23:4 SMART Link alarm level 3 tripped |  | 0 | 1
840 | Alarm 23:10 AQUA Link I/O-module no. 5 com. error |  | 0 | 1
841 | Alarm 23:11 AQUA Link pump monitor tripped |  | 0 | 1
846 | Alarm 24:1 SMART Link no. 1 com. error |  | 0 | 1
847 | Alarm 24:2 SMART Link no. 1 alarm tripped |  | 0 | 1
849 | Alarm 24:4 SMART Link no. 2 com. error |  | 0 | 1
850 | Alarm 24:5 SMART Link no. 2 alarm tripped |  | 0 | 1
852 | Alarm 24:7 SMART Link no. 3 com. error |  | 0 | 1
853 | Alarm 24:8 SMART Link no. 3 alarm tripped |  | 0 | 1
855 | Alarm 24:10 SMART Link no. 4 com. error |  | 0 | 1
856 | Alarm 24:11 SMART Link no. 4 alarm tripped |  | 0 | 1
858 | Alarm 24:13 SMART Link supply air flow below alarm limit |  | 0 | 1 |  |  | 1.25
861 | Alarm 25:1 SMART Link+, cooling circuit A com. error |  | 0 | 1 |  |  | 1.32
862 | Alarm 25:2 SMART Link+, cooling circuit B com. error |  | 0 | 1 |  |  | 1.32
863 | Alarm 25:3 SMART Link+, heating circuit A com. error |  | 0 | 1 |  |  | 1.32
864 | Alarm 25:4 SMART Link+, heating circuit B com. error |  | 0 | 1 |  |  | 1.32
876 | Alarm 26:1 Pre-filter supply air pressure sensor no.8 com. error |  | 0 | 1
877 | Alarm 26:2 Pre-filter supply air dirty |  | 0 | 1
882 | Alarm 26:7 Pre-filter extract air pressure sensor no.9 com. error |  | 0 | 1
883 | Alarm 26:8 Pre-filter extract air dirty |  | 0 | 1
891 | Alarm 27:1 AHU filter supply air pressure sensor no. 3/4 com. error |  | 0 | 1
892 | Alarm 27:2 AHU filter supply air dirty |  | 0 | 1
897 | Alarm 27:7 AHU filter extract air pressure sensor no. 3/4 com. error |  | 0 | 1
898 | Alarm 27:8 AHU filter extract air dirty |  | 0 | 1
906 | Alarm 28:1 End filter supply air pressure sensor no. A com. error |  | 0 | 1
907 | Alarm 28:2 End filter supply air dirty |  | 0 | 1
936 | Alarm 30:1 Air flow measurement supply air pressure sensor no. 1/2 com. error |  | 0 | 1
937 | Alarm 30:2 Air flow measurement supply air flow below set point alarm limit |  | 0 | 1
938 | Alarm 30:3 Air flow measurement supply air flow above set point alarm limit |  | 0 | 1
941 | Alarm 30:6 Air flow measurement extract air pressure sensor no. 1/2 com. error |  | 0 | 1
942 | Alarm 30:7 Air flow measurement extract air flow below set point alarm limit |  | 0 | 1
943 | Alarm 30:8 Air flow measurement extract air flow above set point alarm limit |  | 0 | 1
946 | Alarm 30:11 Air flow meas. carry over control press. sensor no. B com. error |  | 0 | 1
951 | Alarm 31:1 Pressure regulation supply air pressure sensor no. 5 com. error |  | 0 | 1
952 | Alarm 31:2 Pressure regulation supply air pressure below set point alarm limit |  | 0 | 1
953 | Alarm 31:3 Pressure regulation supply air pressure above set point alarm limit |  | 0 | 1
956 | Alarm 31:6 Pressure regulation extract air pressure sensor no. 6 com. error |  | 0 | 1
957 | Alarm 31:7 Pressure regulation extract air press. below set point alarm limit |  | 0 | 1
958 | Alarm 31:8 Pressure regulation extract air press. above set point alarm limit |  | 0 | 1
966 | Alarm 32:1 ReCO2 I/O-module no. 0 com. error |  | 0 | 1
967 | Alarm 32:2 ReCO2 pressure sensor no. 0 com. error |  | 0 | 1
968 | Alarm 32:3 ReCO2 recirculation damper monitoring tripped |  | 0 | 1
969 | Alarm 32:4 ReCO2 outdoor air damper monitoring tripped |  | 0 | 1
981 | Alarm 33:1 Service period above alarm limit |  | 0 | 1
995 | Alarm 33:15 Lock function tripped |  | 0 | 1
996 | Alarm 34:1 External control I/O-module no. 3 com. error |  | 0 | 1
997 | Alarm 34:2 External control I/O-module no. 6 com. error |  | 0 | 1
1011 | Alarm 35:1 Booster diffusers I/O-module no. 8 com. error |  | 0 | 1
1026 | Alarm 36:1 External BMS control I/O-module no. A communication error |  | 0 | 1 |  |  | 1.20
1027 | Alarm 36:2 External BMS control I/O-module no. A temp. sensor no. 1 defective |  | 0 | 1 |  |  | 1.20
1028 | Alarm 36:3 External BMS control I/O-module no. A temp. sensor no. 2 defective |  | 0 | 1 |  |  | 1.20
1031 | Alarm 36:6 External BMS control I/O-module no. B communication error |  | 0 | 1 |  |  | 1.20
1032 | Alarm 36:7 External BMS control I/O-module no. B temp. sensor no. 1 defective |  | 0 | 1 |  |  | 1.20
1033 | Alarm 36:8 External BMS control I/O-module no. B temp. sensor no. 2 defective |  | 0 | 1 |  |  | 1.20
1036 | Alarm 36:11 External BMS control I/O-module no. C communication error |  | 0 | 1 |  |  | 1.20
1037 | Alarm 36:12 External BMS control I/O-module no. C temp. sensor no. 1 defective |  | 0 | 1 |  |  | 1.20
1038 | Alarm 36:13 External BMS control I/O-module no. C temp. sensor no. 2 defective |  | 0 | 1 |  |  | 1.20
1056 | Alarm 38:1 MIRU 1 com. error |  | 0 | 1
1057 | Alarm 38:2 MIRU 1 motor controller alarm tripped |  | 0 | 1
1058 | Alarm 38:3 MIRU 1 motor controller com. error |  | 0 | 1
1059 | Alarm 38:4 MIRU 1 air flow pressure sensor no. 0 com. error |  | 0 | 1
1060 | Alarm 38:5 MIRU 1 pressure regulation sensor no. 1 com. error |  | 0 | 1
1061 | Alarm 38:6 MIRU 1 temperature sensor defective |  | 0 | 1
1062 | Alarm 38:7 MIRU 1 air flow/pressure set point deviation from alarm limit |  | 0 | 1
1063 | Alarm 38:8 MIRU 1 air flow below set point alarm limit |  | 0 | 1 |  |  | 1.25
1064 | Alarm 38:9 MIRU 1 air flow above set point alarm limit |  | 0 | 1 |  |  | 1.25
1065 | Alarm 38:10 MIRU 1 pressure below set point alarm limit |  | 0 | 1 |  |  | 1.25
1066 | Alarm 38:11 MIRU 1 pressure above set point alarm limit |  | 0 | 1 |  |  | 1.25
1071 | Alarm 39:1 MIRU 2 com. error |  | 0 | 1
1072 | Alarm 39:2 MIRU 2 motor controller alarm tripped |  | 0 | 1
1073 | Alarm 39:3 MIRU 2 motor controller com. error |  | 0 | 1
1074 | Alarm 39:4 MIRU 2 air flow pressure sensor no. 0 com. error |  | 0 | 1
1075 | Alarm 39:5 MIRU 2 pressure regulation sensor no. 1 com. error |  | 0 | 1
1076 | Alarm 39:6 MIRU 2 temperature sensor defective |  | 0 | 1
1077 | Alarm 39:7 MIRU 2 air flow/pressure set point deviation from alarm limit |  | 0 | 1
1078 | Alarm 39:8 MIRU 2 air flow below set point alarm limit |  | 0 | 1 |  |  | 1.25
1079 | Alarm 39:9 MIRU 2 air flow above set point alarm limit |  | 0 | 1 |  |  | 1.25
1080 | Alarm 39:10 MIRU 2 pressure below set point alarm limit |  | 0 | 1 |  |  | 1.25
1081 | Alarm 39:11 MIRU 2 pressure above set point alarm limit |  | 0 | 1 |  |  | 1.25
1086 | Alarm 40:1 MIRU 3 com. error |  | 0 | 1
1087 | Alarm 40:2 MIRU 3 motor controller alarm tripped |  | 0 | 1
1088 | Alarm 40:3 MIRU 3 motor controller com. error |  | 0 | 1
1089 | Alarm 40:4 MIRU 3 air flow pressure sensor no. 0 com. error |  | 0 | 1
1090 | Alarm 40:5 MIRU 3 pressure regulation sensor no. 1 com. error |  | 0 | 1
1091 | Alarm 40:6 MIRU 3 temperature sensor defective |  | 0 | 1
1092 | Alarm 40:7 MIRU 3 air flow/pressure set point deviation from alarm limit |  | 0 | 1
1093 | Alarm 40:8 MIRU 3 air flow below set point alarm limit |  | 0 | 1 |  |  | 1.25
1094 | Alarm 40:9 MIRU 3 air flow above set point alarm limit |  | 0 | 1 |  |  | 1.25
1095 | Alarm 40:10 MIRU 3 pressure below set point alarm limit |  | 0 | 1 |  |  | 1.25
1096 | Alarm 40:11 MIRU 3 pressure above set point alarm limit |  | 0 | 1 |  |  | 1.25
1101 | Alarm 41:1 MIRU 4 com. error |  | 0 | 1
1102 | Alarm 41:2 MIRU 4 motor controller alarm tripped |  | 0 | 1
1103 | Alarm 41:3 MIRU 4 motor controller com. error |  | 0 | 1
1104 | Alarm 41:4 MIRU 4 air flow pressure sensor no. 0 com. error |  | 0 | 1
1105 | Alarm 41:5 MIRU 4 pressure regulation sensor no. 1 com. error |  | 0 | 1
1106 | Alarm 41:6 MIRU 4 temperature sensor defective |  | 0 | 1
1107 | Alarm 41:7 MIRU 4 air flow/pressure set point deviation from alarm limit |  | 0 | 1
1116 | Alarm 42:1 MIRU 5 com. error |  | 0 | 1
1117 | Alarm 42:2 MIRU 5 motor controller alarm tripped |  | 0 | 1
1118 | Alarm 42:3 MIRU 5 motor controller com. error |  | 0 | 1
1119 | Alarm 42:4 MIRU 5 air flow pressure sensor no. 0 com. error |  | 0 | 1
1120 | Alarm 42:5 MIRU 5 pressure regulation sensor no. 1 com. error |  | 0 | 1
1121 | Alarm 42:6 MIRU 5 temperature sensor defective |  | 0 | 1
1122 | Alarm 42:7 MIRU 5 air flow/pressure set point deviation from alarm limit |  | 0 | 1
1131 | Alarm 43:1 MIRU 6 com. error |  | 0 | 1
1132 | Alarm 43:2 MIRU 6 motor controller alarm tripped |  | 0 | 1
1133 | Alarm 43:3 MIRU 6 motor controller com. error |  | 0 | 1
1134 | Alarm 43:4 MIRU 6 air flow pressure sensor no. 0 com. error |  | 0 | 1
1135 | Alarm 43:5 MIRU 6 pressure regulation sensor no. 1 com. error |  | 0 | 1
1136 | Alarm 43:6 MIRU 6 temperature sensor defective |  | 0 | 1
1137 | Alarm 43:7 MIRU 6 air flow/pressure set point deviation from alarm limit |  | 0 | 1
1146 | Alarm 44:1 MIRU 7 com. error |  | 0 | 1
1147 | Alarm 44:2 MIRU 7 motor controller alarm tripped |  | 0 | 1
1148 | Alarm 44:3 MIRU 7 motor controller com. error |  | 0 | 1
1149 | Alarm 44:4 MIRU 7 air flow pressure sensor no. 0 com. error |  | 0 | 1
1150 | Alarm 44:5 MIRU 7 pressure regulation sensor no. 1 com. error |  | 0 | 1
1151 | Alarm 44:6 MIRU 7 temperature sensor defective |  | 0 | 1
1152 | Alarm 44:7 MIRU 7 air flow/pressure set point deviation from alarm limit |  | 0 | 1
1161 | Alarm 45:1 MIRU 8 com. error |  | 0 | 1
1162 | Alarm 45:2 MIRU 8 motor controller alarm tripped |  | 0 | 1
1163 | Alarm 45:3 MIRU 8 motor controller com. error |  | 0 | 1
1164 | Alarm 45:4 MIRU 8 air flow pressure sensor no. 0 com. error |  | 0 | 1
1165 | Alarm 45:5 MIRU 8 pressure regulation sensor no. 1 com. error |  | 0 | 1
1166 | Alarm 45:6 MIRU 8 temperature sensor defective |  | 0 | 1
1167 | Alarm 45:7 MIRU 8 air flow/pressure set point deviation from alarm limit |  | 0 | 1
1176 | Alarm 46:1 MIRU 9 com. error |  | 0 | 1
1177 | Alarm 46:2 MIRU 9 motor controller alarm tripped |  | 0 | 1
1178 | Alarm 46:3 MIRU 9 motor controller com. error |  | 0 | 1
1179 | Alarm 46:4 MIRU 9 air flow pressure sensor no. 0 com. error |  | 0 | 1
1180 | Alarm 46:5 MIRU 9 pressure regulation sensor no. 1 com. error |  | 0 | 1
1181 | Alarm 46:6 MIRU 9 temperature sensor defective |  | 0 | 1
1182 | Alarm 46:7 MIRU 9 air flow/pressure set point deviation from alarm limit |  | 0 | 1
1191 | Alarm 47:1 MIRU 10 com. error |  | 0 | 1
1192 | Alarm 47:2 MIRU 10 motor controller alarm tripped |  | 0 | 1
1193 | Alarm 47:3 MIRU 10 motor controller com. error |  | 0 | 1
1194 | Alarm 47:4 MIRU 10 air flow pressure sensor no. 0 com. error |  | 0 | 1
1195 | Alarm 47:5 MIRU 10 pressure regulation sensor no. 1 com. error |  | 0 | 1
1196 | Alarm 47:6 MIRU 10 temperature sensor defective |  | 0 | 1
1197 | Alarm 47:7 MIRU 10 air flow/pressure set point deviation from alarm limit |  | 0 | 1
1221 | Alarm 49:1 Supply air fan no. 1A com. error |  | 0 | 1
1222 | Alarm 49:2 Supply air fan no. 1A motor controller over current |  | 0 | 1
1223 | Alarm 49:3 Supply air fan no. 1A motor controller under voltage |  | 0 | 1
1224 | Alarm 49:4 Supply air fan no. 1A motor controller over voltage |  | 0 | 1
1225 | Alarm 49:5 Supply air fan no. 1A motor controller over temperature |  | 0 | 1
1226 | Alarm 49:6 Supply air fan no. 1A motor controller start error |  | 0 | 1
1227 | Alarm 49:7 Supply air fan no. 1A motor controller ripple error |  | 0 | 1
1228 | Alarm 49:8 Supply air fan no. 1A motor controller phase error |  | 0 | 1
1229 | Alarm 49:9 Supply air fan no. 1A motor controller internal memory error |  | 0 | 1
1230 | Alarm 49:10 Supply air fan no. 1A motor controller current reduction |  | 0 | 1
1231 | Alarm 49:11 Supply air fan no. 1A motor controller internal com. error |  | 0 | 1 |  |  | 1.18
1236 | Alarm 50:1 Supply air fan no. 2A com. error |  | 0 | 1
1237 | Alarm 50:2 Supply air fan no. 2A motor controller over current |  | 0 | 1
1238 | Alarm 50:3 Supply air fan no. 2A motor controller under voltage |  | 0 | 1
1239 | Alarm 50:4 Supply air fan no. 2A motor controller over voltage |  | 0 | 1
1240 | Alarm 50:5 Supply air fan no. 2A motor controller over temperature |  | 0 | 1
1241 | Alarm 50:6 Supply air fan no. 2A motor controller start error |  | 0 | 1
1242 | Alarm 50:7 Supply air fan no. 2A motor controller ripple error |  | 0 | 1
1243 | Alarm 50:8 Supply air fan no. 2A motor controller phase error |  | 0 | 1
1244 | Alarm 50:9 Supply air fan no. 2A motor controller internal memory error |  | 0 | 1
1245 | Alarm 50:10 Supply air fan no. 2A motor controller current reduction |  | 0 | 1
1246 | Alarm 50:11 Supply air fan no. 2A motor controller internal com. Error |  | 0 | 1 |  |  | 1.18
1251 | Alarm 51:1 Supply air fan no. 3A com. error |  | 0 | 1
1252 | Alarm 51:2 Supply air fan no. 3A motor controller over current |  | 0 | 1
1253 | Alarm 51:3 Supply air fan no. 3A motor controller under voltage |  | 0 | 1
1254 | Alarm 51:4 Supply air fan no. 3A motor controller over voltage |  | 0 | 1
1255 | Alarm 51:5 Supply air fan no. 3A motor controller over temperature |  | 0 | 1
1256 | Alarm 51:6 Supply air fan no. 3A motor controller start error |  | 0 | 1
1257 | Alarm 51:7 Supply air fan no. 3A motor controller ripple error |  | 0 | 1
1258 | Alarm 51:8 Supply air fan no. 3A motor controller phase error |  | 0 | 1
1259 | Alarm 51:9 Supply air fan no. 3A motor controller internal memory error |  | 0 | 1
1260 | Alarm 51:10 Supply air fan no. 3A motor controller current reduction |  | 0 | 1
1261 | Alarm 51:11 Supply air fan no. 3A motor controller internal com. error |  | 0 | 1 |  |  | 1.18
1266 | Alarm 52:1 Supply air fan no. 1B com. error |  | 0 | 1
1267 | Alarm 52:2 Supply air fan no. 1B motor controller over current |  | 0 | 1
1268 | Alarm 52:3 Supply air fan no. 1B motor controller under voltage |  | 0 | 1
1269 | Alarm 52:4 Supply air fan no. 1B motor controller over voltage |  | 0 | 1
1270 | Alarm 52:5 Supply air fan no. 1B motor controller over temperature |  | 0 | 1
1271 | Alarm 52:6 Supply air fan no. 1B motor controller start error |  | 0 | 1
1272 | Alarm 52:7 Supply air fan no. 1B motor controller ripple error |  | 0 | 1
1273 | Alarm 52:8 Supply air fan no. 1B motor controller phase error |  | 0 | 1
1274 | Alarm 52:9 Supply air fan no. 1B motor controller internal memory error |  | 0 | 1
1275 | Alarm 52:10 Supply air fan no. 1B motor controller current reduction |  | 0 | 1
1281 | Alarm 53:1 Supply air fan no. 2B com. error |  | 0 | 1
1282 | Alarm 53:2 Supply air fan no. 2B motor controller over current |  | 0 | 1
1283 | Alarm 53:3 Supply air fan no. 2B motor controller under voltage |  | 0 | 1
1284 | Alarm 53:4 Supply air fan no. 2B motor controller over voltage |  | 0 | 1
1285 | Alarm 53:5 Supply air fan no. 2B motor controller over temperature |  | 0 | 1
1286 | Alarm 53:6 Supply air fan no. 2B motor controller start error |  | 0 | 1
1287 | Alarm 53:7 Supply air fan no. 2B motor controller ripple error |  | 0 | 1
1288 | Alarm 53:8 Supply air fan no. 2B motor controller phase error |  | 0 | 1
1289 | Alarm 53:9 Supply air fan no. 2B motor controller internal memory error |  | 0 | 1
1290 | Alarm 53:10 Supply air fan no. 2B motor controller current reduction |  | 0 | 1
1296 | Alarm 54:1 Supply air fan no. 3B com. error |  | 0 | 1
1297 | Alarm 54:2 Supply air fan no. 3B motor controller over current |  | 0 | 1
1298 | Alarm 54:3 Supply air fan no. 3B motor controller under voltage |  | 0 | 1
1299 | Alarm 54:4 Supply air fan no. 3B motor controller over voltage |  | 0 | 1
1300 | Alarm 54:5 Supply air fan no. 3B motor controller over temperature |  | 0 | 1
1301 | Alarm 54:6 Supply air fan no. 3B motor controller start error |  | 0 | 1
1302 | Alarm 54:7 Supply air fan no. 3B motor controller ripple error |  | 0 | 1
1303 | Alarm 54:8 Supply air fan no. 3B motor controller phase error |  | 0 | 1
1304 | Alarm 54:9 Supply air fan no. 3B motor controller internal memory error |  | 0 | 1
1305 | Alarm 54:10 Supply air fan no. 3B motor controller current reduction |  | 0 | 1
1311 | Alarm 55:1 Extract air fan no. 1A com. error |  | 0 | 1
1312 | Alarm 55:2 Extract air fan no. 1A motor controller over current |  | 0 | 1
1313 | Alarm 55:3 Extract air fan no. 1A motor controller under voltage |  | 0 | 1
1314 | Alarm 55:4 Extract air fan no. 1A motor controller over voltage |  | 0 | 1
1315 | Alarm 55:5 Extract air fan no. 1A motor controller over temperature |  | 0 | 1
1316 | Alarm 55:6 Extract air fan no. 1A motor controller start error |  | 0 | 1
1317 | Alarm 55:7 Extract air fan no. 1A motor controller ripple error |  | 0 | 1
1318 | Alarm 55:8 Extract air fan no. 1A motor controller phase error |  | 0 | 1
1319 | Alarm 55:9 Extract air fan no. 1A motor controller internal memory error |  | 0 | 1
1320 | Alarm 55:10 Extract air fan no. 1A motor controller current reduction |  | 0 | 1
1321 | Alarm 55:11 Extract air fan no. 1A motor controller internal com. error |  | 0 | 1 |  |  | 1.18
1326 | Alarm 56:1 Extract air fan no. 2A com. error |  | 0 | 1
1327 | Alarm 56:2 Extract air fan no. 2A motor controller over current |  | 0 | 1
1328 | Alarm 56:3 Extract air fan no. 2A motor controller under voltage |  | 0 | 1
1329 | Alarm 56:4 Extract air fan no. 2A motor controller over voltage |  | 0 | 1
1330 | Alarm 56:5 Extract air fan no. 2A motor controller over temperature |  | 0 | 1
1331 | Alarm 56:6 Extract air fan no. 2A motor controller start error |  | 0 | 1
1332 | Alarm 56:7 Extract air fan no. 2A motor controller ripple error |  | 0 | 1
1333 | Alarm 56:8 Extract air fan no. 2A motor controller phase error |  | 0 | 1
1334 | Alarm 56:9 Extract air fan no. 2A motor controller internal memory error |  | 0 | 1
1335 | Alarm 56:10 Extract air fan no. 2A motor controller current reduction |  | 0 | 1
1336 | Alarm 56:11 Extract air fan no. 2A motor controller internal com. Error |  | 0 | 1 |  |  | 1.18
1341 | Alarm 57:1 Extract air fan no. 3A com. error |  | 0 | 1
1342 | Alarm 57:2 Extract air fan no. 3A motor controller over current |  | 0 | 1
1343 | Alarm 57:3 Extract air fan no. 3A motor controller under voltage |  | 0 | 1
1344 | Alarm 57:4 Extract air fan no. 3A motor controller over voltage |  | 0 | 1
1345 | Alarm 57:5 Extract air fan no. 3A motor controller over temperature |  | 0 | 1
1346 | Alarm 57:6 Extract air fan no. 3A motor controller start error |  | 0 | 1
1347 | Alarm 57:7 Extract air fan no. 3A motor controller ripple error |  | 0 | 1
1348 | Alarm 57:8 Extract air fan no. 3A motor controller phase error |  | 0 | 1
1349 | Alarm 57:9 Extract air fan no. 3A motor controller internal memory error |  | 0 | 1
1350 | Alarm 57:10 Extract air fan no. 3A motor controller current reduction |  | 0 | 1
1351 | Alarm 57:11 Extract air fan no. 3A motor controller internal com. error |  | 0 | 1 |  |  | 1.18
1356 | Alarm 58:1 Extract air fan no. 1B com. error |  | 0 | 1
1357 | Alarm 58:2 Extract air fan no. 1B motor controller over current |  | 0 | 1
1358 | Alarm 58:3 Extract air fan no. 1B motor controller under voltage |  | 0 | 1
1359 | Alarm 58:4 Extract air fan no. 1B motor controller over voltage |  | 0 | 1
1360 | Alarm 58:5 Extract air fan no. 1B motor controller over temperature |  | 0 | 1
1361 | Alarm 58:6 Extract air fan no. 1B motor controller start error |  | 0 | 1
1362 | Alarm 58:7 Extract air fan no. 1B motor controller ripple error |  | 0 | 1
1363 | Alarm 58:8 Extract air fan no. 1B motor controller phase error |  | 0 | 1
1364 | Alarm 58:9 Extract air fan no. 1B motor controller internal memory error |  | 0 | 1
1365 | Alarm 58:10 Extract air fan no. 1B motor controller current reduction |  | 0 | 1
1371 | Alarm 59:1 Extract air fan no. 2B com. error |  | 0 | 1
1372 | Alarm 59:2 Extract air fan no. 2B motor controller over current |  | 0 | 1
1373 | Alarm 59:3 Extract air fan no. 2B motor controller under voltage |  | 0 | 1
1374 | Alarm 59:4 Extract air fan no. 2B motor controller over voltage |  | 0 | 1
1375 | Alarm 59:5 Extract air fan no. 2B motor controller over temperature |  | 0 | 1
1376 | Alarm 59:6 Extract air fan no. 2B motor controller start error |  | 0 | 1
1377 | Alarm 59:7 Extract air fan no. 2B motor controller ripple error |  | 0 | 1
1378 | Alarm 59:8 Extract air fan no. 2B motor controller phase error |  | 0 | 1
1379 | Alarm 59:9 Extract air fan no. 2B motor controller internal memory error |  | 0 | 1
1380 | Alarm 59:10 Extract air fan no. 2B motor controller current reduction |  | 0 | 1
1386 | Alarm 60:1 Extract air fan no. 3B com. error |  | 0 | 1
1387 | Alarm 60:2 Extract air fan no. 3B motor controller over current |  | 0 | 1
1388 | Alarm 60:3 Extract air fan no. 3B motor controller under voltage |  | 0 | 1
1389 | Alarm 60:4 Extract air fan no. 3B motor controller over voltage |  | 0 | 1
1390 | Alarm 60:5 Extract air fan no. 3B motor controller over temperature |  | 0 | 1
1391 | Alarm 60:6 Extract air fan no. 3B motor controller start error |  | 0 | 1
1392 | Alarm 60:7 Extract air fan no. 3B motor controller ripple error |  | 0 | 1
1393 | Alarm 60:8 Extract air fan no. 3B motor controller phase error |  | 0 | 1
1394 | Alarm 60:9 Extract air fan no. 3B motor controller internal memory error |  | 0 | 1
1395 | Alarm 60:10 Extract air fan no. 3B motor controller current reduction |  | 0 | 1
1401 | Alarm 61:1 Supply air fan no. 1A I/O-module com. error |  | 0 | 1 |  |  | 1.18
1406 | Alarm 61:6 Supply air fan no. 2A I/O-module com. error |  | 0 | 1 |  |  | 1.18
1411 | Alarm 61:11 Supply air fan no. 3A I/O-module com. error |  | 0 | 1 |  |  | 1.18
1416 | Alarm 62:1 Extract air fan no. 1A I/O-module com. error |  | 0 | 1 |  |  | 1.18
1421 | Alarm 62:6 Extract air fan no. 2A I/O-module com. error |  | 0 | 1 |  |  | 1.18
1426 | Alarm 62:11 Extract air fan no. 3A I/O-module com. error |  | 0 | 1 |  |  | 1.18
1431 | Alarm 63:1 MIRU 1 I/O-module com. Error |  | 0 | 1 |  |  | 1.25
1436 | Alarm 63:6 MIRU 2 I/O-module com. Error |  | 0 | 1 |  |  | 1.25
1441 | Alarm 63:11 MIRU 3 I/O-module com. Error |  | 0 | 1 |  |  | 1.25
1446 | Alarm 64:1 Supply air fan no. 1A common A-alarm |  | 0 | 1 |  |  | 2.40
1448 | Alarm 64:3 Supply air fan no. 1A common B-alarm |  | 0 | 1 |  |  | 2.40
1450 | Alarm 64:5 Supply air fan no. 1A common warning |  | 0 | 1 |  |  | 2.40
1451 | Alarm 64:6 Supply air fan no. 2A common A-alarm |  | 0 | 1 |  |  | 2.40
1453 | Alarm 64:8 Supply air fan no. 2A common B-alarm |  | 0 | 1 |  |  | 2.40
1455 | Alarm 64:10 Supply air fan no. 2A common warning |  | 0 | 1 |  |  | 2.40
1456 | Alarm 64:11 Supply air fan no. 3A common A-alarm |  | 0 | 1 |  |  | 2.40
1458 | Alarm 64:13 Supply air fan no. 3A common B-alarm |  | 0 | 1 |  |  | 2.40
1460 | Alarm 64:15 Supply air fan no. 3A common warning |  | 0 | 1 |  |  | 2.40
1461 | Alarm 65:1 Extract air fan no. 1A common A-alarm |  | 0 | 1 |  |  | 2.40
1463 | Alarm 65:3 Extract air fan no. 1A common B-alarm |  | 0 | 1 |  |  | 2.40
1465 | Alarm 65:5 Extract air fan no. 1A common warning |  | 0 | 1 |  |  | 2.40
1466 | Alarm 65:6 Extract air fan no. 2A common A-alarm |  | 0 | 1 |  |  | 2.40
1468 | Alarm 65:8 Extract air fan no. 2A common B-alarm |  | 0 | 1 |  |  | 2.40
1470 | Alarm 65:10 Extract air fan no. 2A common warning |  | 0 | 1 |  |  | 2.40
1471 | Alarm 65:11 Extract air fan no. 3A common A-alarm |  | 0 | 1 |  |  | 2.40
1473 | Alarm 65:13 Extract air fan no. 3A common B-alarm |  | 0 | 1 |  |  | 2.40
1475 | Alarm 65:15 Extract air fan no. 3A common warning |  | 0 | 1 |  |  | 2.40
1537 | Alarm 70:2 H/C controls internal memory error |  | 0 | 1 |  |  | 1.23
1538 | Alarm 70:3 H/C controls clock circuit defective |  | 0 | 1 |  |  | 1.23
1540 | Alarm 70:5 H/C defrost pressure sensor no. D com. error |  | 0 | 1 |  |  | 1.23
1541 | Alarm 70:6 H/C defrost I/O-module no. 5 com. error |  | 0 | 1 |  |  | 1.23
1542 | Alarm 70:7 H/C defrost recirculation damper monitoring tripped |  | 0 | 1 |  |  | 1.23
1543 | Alarm 70:8 H/C defrost electrical heater overheat protection tripped |  | 0 | 1 |  |  | 1.23
1544 | Alarm 70:9 H/C defrost time above alarm limit |  | 0 | 1 |  |  | 1.23
1546 | Alarm 70:11 H/C defrost interval above alarm limit |  | 0 | 1 |  |  | 1.27
1547 | Alarm 70:12 H/C wrong phase sequence |  | 0 | 1 |  |  | 1.27
1551 | Alarm 71:1 H/C compressor motor control com. error |  | 0 | 1 |  |  | 1.23
1552 | Alarm 71:2 H/C compressor motor control start error |  | 0 | 1 |  |  | 1.23
1553 | Alarm 71:3 H/C compressor motor controller over or under voltage |  | 0 | 1 |  |  | 1.23
1554 | Alarm 71:4 H/C compressor out of operation range |  | 0 | 1 |  |  | 1.23
1559 | Alarm 71:9 H/C expansion valve controller com. error |  | 0 | 1 |  |  | 1.23
1566 | Alarm 72:1 H/C high pressure switch tripped |  | 0 | 1 |  |  | 1.23
1567 | Alarm 72:2 H/C high pressure above alarm limit |  | 0 | 1 |  |  | 1.23
1568 | Alarm 72:3 H/C thermal switch tripped |  | 0 | 1 |  |  | 1.23
1569 | Alarm 72:4 H/C discharge temperature above alarm limit |  | 0 | 1 |  |  | 1.23
1570 | Alarm 72:5 H/C discharge temperature sensor defective |  | 0 | 1 |  |  | 1.23
1571 | Alarm 72:6 H/C high pressure sensor defective |  | 0 | 1 |  |  | 1.23
1572 | Alarm 72:7 H/C low pressure sensor defective |  | 0 | 1 |  |  | 1.23
1573 | Alarm 72:8 H/C suction temperature sensor defective |  | 0 | 1 |  |  | 1.23
1574 | Alarm 72:9 H/C pressure difference below alarm limit |  | 0 | 1 |  |  | 1.23
1575 | Alarm 72:10 H/C maintenance and compressor |  | 0 | 1 |  |  | 1.23
1576 | Alarm 72:11 H/C superheat temperature below alarm limit |  | 0 | 1 |  |  | 1.23
1577 | Alarm 72:12 H/C unloading of low pressure |  | 0 | 1 |  |  | 1.23
1578 | Alarm 72:13 H/C unloading of high pressure |  | 0 | 1 |  |  | 1.23
1579 | Alarm 72:14 H/C low pressure below alarm limit |  | 0 | 1 |  |  | 1.23
1642 | Alarm 77:2 MIRU 1 motor controller over current |  | 0 | 1 |  |  | 1.25
1643 | Alarm 77:3 MIRU 1 motor controller under voltage |  | 0 | 1 |  |  | 1.25
1644 | Alarm 77:4 MIRU 1 motor controller over voltage |  | 0 | 1 |  |  | 1.25
1645 | Alarm 77:5 MIRU 1 motor controller over temperature |  | 0 | 1 |  |  | 1.25
1646 | Alarm 77:6 MIRU 1 motor controller start error |  | 0 | 1 |  |  | 1.25
1647 | Alarm 77:7 MIRU 1 motor controller ripple error |  | 0 | 1 |  |  | 1.25
1648 | Alarm 77:8 MIRU 1 motor controller phase error |  | 0 | 1 |  |  | 1.25
1649 | Alarm 77:9 MIRU 1 motor controller internal memory error |  | 0 | 1 |  |  | 1.25
1650 | Alarm 77:10 MIRU 1 motor controller current reduction |  | 0 | 1 |  |  | 1.25
1651 | Alarm 77:11 MIRU 1 motor controller internal com. Error |  | 0 | 1 |  |  | 1.25
1657 | Alarm 78:2 MIRU 2 motor controller over current |  | 0 | 1 |  |  | 1.25
1658 | Alarm 78:3 MIRU 2 motor controller under voltage |  | 0 | 1 |  |  | 1.25
1659 | Alarm 78:4 MIRU 2 motor controller over voltage |  | 0 | 1 |  |  | 1.25
1660 | Alarm 78:5 MIRU 2 motor controller over temperature |  | 0 | 1 |  |  | 1.25
1661 | Alarm 78:6 MIRU 2 motor controller start error |  | 0 | 1 |  |  | 1.25
1662 | Alarm 78:7 MIRU 2 motor controller ripple error |  | 0 | 1 |  |  | 1.25
1663 | Alarm 78:8 MIRU 2 motor controller phase error |  | 0 | 1 |  |  | 1.25
1664 | Alarm 78:9 MIRU 2 motor controller internal memory error |  | 0 | 1 |  |  | 1.25
1665 | Alarm 78:10 MIRU 2 motor controller current reduction |  | 0 | 1 |  |  | 1.25
1666 | Alarm 78:11 MIRU 2 motor controller internal com. Error |  | 0 | 1 |  |  | 1.25
1672 | Alarm 79:2 MIRU 3 motor controller over current |  | 0 | 1 |  |  | 1.25
1673 | Alarm 79:3 MIRU 3 motor controller under voltage |  | 0 | 1 |  |  | 1.25
1674 | Alarm 79:4 MIRU 3 motor controller over voltage |  | 0 | 1 |  |  | 1.25
1675 | Alarm 79:5 MIRU 3 motor controller over temperature |  | 0 | 1 |  |  | 1.25
1676 | Alarm 79:6 MIRU 3 motor controller start error |  | 0 | 1 |  |  | 1.25
1677 | Alarm 79:7 MIRU 3 motor controller ripple error |  | 0 | 1 |  |  | 1.25
1678 | Alarm 79:8 MIRU 3 motor controller phase error |  | 0 | 1 |  |  | 1.25
1679 | Alarm 79:9 MIRU 3 motor controller internal memory error |  | 0 | 1 |  |  | 1.25
1680 | Alarm 79:10 MIRU 3 motor controller current reduction |  | 0 | 1 |  |  | 1.25
1681 | Alarm 79:11 MIRU 3 motor controller internal com. Error |  | 0 | 1 |  |  | 1.25
1702 | Alarm 81:2 SMART Link no. 1 supply air flow below defrost alarm limit |  | 0 | 1 |  |  | 1.25
1703 | Alarm 81:3 SMART Link no. 1 High pressure switch tripped |  | 0 | 1 |  |  | 1.27
1704 | Alarm 81:4 SMART Link no. 1 High pressure above alarm limit |  | 0 | 1 |  |  | 1.27
1705 | Alarm 81:5 SMART Link no. 1 Low pressure below alarm limit |  | 0 | 1 |  |  | 1.27
1706 | Alarm 81:6 SMART Link no. 1 Evaporation temperature below alarm limit |  | 0 | 1 |  |  | 1.27
1707 | Alarm 81:7 SMART Link no. 1 Inverter group alarm (Power+) |  | 0 | 1 |  |  | 1.27
1708 | Alarm 81:8 SMART Link no. 1 Envelope alarm |  | 0 | 1 |  |  | 1.27
1709 | Alarm 81:9 SMART Link no. 1 Starting up of faulty compressor |  | 0 | 1 |  |  | 1.27
1710 | Alarm 81:10 SMART Link no. 1 Discharge temperature above alarm limit |  | 0 | 1 |  |  | 1.27
1711 | Alarm 81:11 SMART Link no. 1 Pressure difference below alarm limit |  | 0 | 1 |  |  | 1.27
1717 | Alarm 82:2 SMART Link no. 2 supply air flow below defrost alarm limit |  | 0 | 1 |  |  | 1.25
1718 | Alarm 82:3 SMART Link no. 2 High pressure switch tripped |  | 0 | 1 |  |  | 1.27
1719 | Alarm 82:4 SMART Link no. 2 High pressure above alarm limit |  | 0 | 1 |  |  | 1.27
1720 | Alarm 82:5 SMART Link no. 2 Low pressure below alarm limit |  | 0 | 1 |  |  | 1.27
1721 | Alarm 82:6 SMART Link no. 2 Evaporation temperature below alarm limit |  | 0 | 1 |  |  | 1.27
1722 | Alarm 82:7 SMART Link no. 2 Inverter group alarm (Power+) |  | 0 | 1 |  |  | 1.27
1723 | Alarm 82:8 SMART Link no. 2 Envelope alarm |  | 0 | 1 |  |  | 1.27
1724 | Alarm 82:9 SMART Link no. 2 Starting up of faulty compressor |  | 0 | 1 |  |  | 1.27
1725 | Alarm 82:10 SMART Link no. 2 Discharge temperature above alarm limit |  | 0 | 1 |  |  | 1.27
1726 | Alarm 82:11 SMART Link no. 2 Pressure difference below alarm limit |  | 0 | 1 |  |  | 1.27
1732 | Alarm 83:2 SMART Link no. 3 supply air flow below defrost alarm limit |  | 0 | 1 |  |  | 1.25
1733 | Alarm 83:3 SMART Link no. 3 High pressure switch tripped |  | 0 | 1 |  |  | 1.27
1734 | Alarm 83:4 SMART Link no. 3 High pressure above alarm limit |  | 0 | 1 |  |  | 1.27
1735 | Alarm 83:5 SMART Link no. 3 Low pressure below alarm limit |  | 0 | 1 |  |  | 1.27
1736 | Alarm 83:6 SMART Link no. 3 Evaporation temperature below alarm limit |  | 0 | 1 |  |  | 1.27
1737 | Alarm 83:7 SMART Link no. 3 Inverter group alarm (Power+) |  | 0 | 1 |  |  | 1.27
1738 | Alarm 83:8 SMART Link no. 3 Envelope alarm |  | 0 | 1 |  |  | 1.27
1739 | Alarm 83:9 SMART Link no. 3 Starting up of faulty compressor |  | 0 | 1 |  |  | 1.27
1740 | Alarm 83:10 SMART Link no. 3 Discharge temperature above alarm limit |  | 0 | 1 |  |  | 1.27
1741 | Alarm 83:11 SMART Link no. 3 Pressure difference below alarm limit |  | 0 | 1 |  |  | 1.27
1747 | Alarm 84:2 SMART Link no. 4 supply air flow below defrost alarm limit |  | 0 | 1 |  |  | 1.25
1748 | Alarm 84:3 SMART Link no. 4 High pressure switch tripped |  | 0 | 1 |  |  | 1.27
1749 | Alarm 84:4 SMART Link no. 4 High pressure above alarm limit |  | 0 | 1 |  |  | 1.27
1750 | Alarm 84:5 SMART Link no. 4 Low pressure below alarm limit |  | 0 | 1 |  |  | 1.27
1751 | Alarm 84:6 SMART Link no. 4 Evaporation temperature below alarm limit |  | 0 | 1 |  |  | 1.27
1752 | Alarm 84:7 SMART Link no. 4 Inverter group alarm (Power+) |  | 0 | 1 |  |  | 1.27
1753 | Alarm 84:8 SMART Link no. 4 Envelope alarm |  | 0 | 1 |  |  | 1.27
1754 | Alarm 84:9 SMART Link no. 4 Starting up of faulty compressor |  | 0 | 1 |  |  | 1.27
1755 | Alarm 84:10 SMART Link no. 4 Discharge temperature above alarm limit |  | 0 | 1 |  |  | 1.27
1756 | Alarm 84:11 SMART Link no. 4 Pressure difference below alarm limit |  | 0 | 1 |  |  | 1.27
1911 | Alarm 95:1 Supply air pre filter calibration performed at low air flow |  | 0 | 1 |  |  | 2.40
1912 | Alarm 95:2 Extract air pre filter calibration performed at low air flow |  | 0 | 1 |  |  | 2.40
1913 | Alarm 95:3 Supply air air handling unit filter calibration performed at low air flow |  | 0 | 1 |  |  | 2.40
1914 | Alarm 95:4 Extract air air handling unit filter calibration performed at low air flow |  | 0 | 1 |  |  | 2.40
1915 | Alarm 95:5 End filter calibration performed at low air flow |  | 0 | 1 |  |  | 2.40
1926 | Alarm 96:1 H/C defrost calibration not performed |  | 0 | 1 |  |  | 1.27
1927 | Alarm 96:2 H/C defrost calibration not approved |  | 0 | 1 |  |  | 1.27
1928 | Alarm 96:3 H/C minimum SA flow limit below factory setting |  | 0 | 1 |  |  | 1.27
1929 | Alarm 96:4 H/C minimum EA flow limit below factory setting |  | 0 | 1 |  |  | 1.27
1930 | Alarm 96:5 H/C OA temp limit for heating below factory setting |  | 0 | 1 |  |  | 1.27
1952 | Info 97:12 Plate heat exchanger bypass optimization not performed |  | 0 | 1 |  |  | 1.13
1953 | Info 97:13 Plate heat exchanger bypass optimization not approved |  | 0 | 1 |  |  | 1.13
1954 | Info 97:14 Plate heat exchanger defrost calibration not performed |  | 0 | 1 |  |  | 1.13
1955 | Info 97:15 Plate heat exchanger defrost calibration not approved |  | 0 | 1 |  |  | 1.13
1956 | Info 98:1 Supply air pre-filter calibration not performed |  | 0 | 1
1957 | Info 98:2 Supply air pre-filter calibration not approved |  | 0 | 1
1958 | Info 98:3 Extract air pre-filter calibration not performed |  | 0 | 1
1959 | Info 98:4 Extract air pre-filter calibration not approved |  | 0 | 1
1960 | Info 98:5 Supply air air handling unit filter calibration not performed |  | 0 | 1
1961 | Info 98:6 Supply air air handling unit filter calibration not approved |  | 0 | 1
1962 | Info 98:7 Extract air air handling unit filter calibration not performed |  | 0 | 1
1963 | Info 98:8 Extract air air handling unit filter calibration not approved |  | 0 | 1
1964 | Info 98:9 Supply air end filter calibration not performed |  | 0 | 1
1965 | Info 98:10 Supply air end filter calibration not approved |  | 0 | 1
1966 | Info 98:11 Rotary heat exchanger defrost calibration not performed |  | 0 | 1
1967 | Info 98:12 Rotary heat exchanger defrost calibration not approved |  | 0 | 1
1968 | Info 98:13 ReCO2 calibration not performed |  | 0 | 1
1969 | Info 98:14 ReCO2 calibration not approved |  | 0 | 1
1970 | Info 98:15 ReCO2 incorrect setting |  | 0 | 1
1971 | Info 99:1 E-mail error |  | 0 | 1
1975 | Info 99:5 FTP error |  | 0 | 1 |  |  | 1.22
1976 | Info 99:6 Schedule invalid data auto corrected |  | 0 | 1 |  |  | 2.36
1977 | Info 99:7 SD card memory soon full. Oldest log data will soon be deleted |  | 0 | 1
1978 | Info 99:8 SD card memory full. Oldest log data deleted |  | 0 | 1
1981 | Info 99:11 No external outdoor air temp. sensor connected for heat retention |  | 0 | 1 |  |  | 1.26
1982 | Info 99:12 No extract air/room temperature sensor connected |  | 0 | 1 |  |  | 1.32
1984 | Info 99:14 Internal serial memory error CPU 1 |  | 0 | 1
1985 | Info 99:15 Clock circuit defective |  | 0 | 1
2001 | Active alarm group 1 |  | 0 | 1
2002 | Active alarm group 2 |  | 0 | 1
2003 | Active alarm group 3 |  | 0 | 1
2004 | Active alarm group 4 |  | 0 | 1
2005 | Active alarm group 5 |  | 0 | 1
2006 | Active alarm group 6 |  | 0 | 1
2007 | Active alarm group 7 |  | 0 | 1
2008 | Active alarm group 8 |  | 0 | 1
2009 | Active alarm group 9 |  | 0 | 1
2010 | Active alarm group 10 |  | 0 | 1
2011 | Active alarm group 11 |  | 0 | 1
2012 | Active alarm group 12 |  | 0 | 1
2013 | Active alarm group 13 |  | 0 | 1
2014 | Active alarm group 14 |  | 0 | 1
2015 | Active alarm group 15 |  | 0 | 1
2016 | Active alarm group 16 |  | 0 | 1
2017 | Active alarm group 17 |  | 0 | 1
2018 | Active alarm group 18 |  | 0 | 1
2019 | Active alarm group 19 |  | 0 | 1
2020 | Active alarm group 20 |  | 0 | 1
2021 | Active alarm group 21 |  | 0 | 1
2022 | Active alarm group 22 |  | 0 | 1
2023 | Active alarm group 23 |  | 0 | 1
2024 | Active alarm group 24 |  | 0 | 1
2025 | Active alarm group 25 |  | 0 | 1
2026 | Active alarm group 26 |  | 0 | 1
2027 | Active alarm group 27 |  | 0 | 1
2028 | Active alarm group 28 |  | 0 | 1
2029 | Active alarm group 29 |  | 0 | 1
2030 | Active alarm group 30 |  | 0 | 1
2031 | Active alarm group 31 |  | 0 | 1
2032 | Active alarm group 32 |  | 0 | 1
2033 | Active alarm group 33 |  | 0 | 1
2034 | Active alarm group 34 |  | 0 | 1
2035 | Active alarm group 35 |  | 0 | 1
2036 | Active alarm group 36 |  | 0 | 1
2037 | Active alarm group 37 |  | 0 | 1
2038 | Active alarm group 38 |  | 0 | 1
2039 | Active alarm group 39 |  | 0 | 1
2040 | Active alarm group 40 |  | 0 | 1
2041 | Active alarm group 41 |  | 0 | 1
2042 | Active alarm group 42 |  | 0 | 1
2043 | Active alarm group 43 |  | 0 | 1
2044 | Active alarm group 44 |  | 0 | 1
2045 | Active alarm group 45 |  | 0 | 1
2046 | Active alarm group 46 |  | 0 | 1
2047 | Active alarm group 47 |  | 0 | 1
2048 | Active alarm group 48 |  | 0 | 1
2049 | Active alarm group 49 |  | 0 | 1
2050 | Active alarm group 50 |  | 0 | 1
2051 | Active alarm group 51 |  | 0 | 1
2052 | Active alarm group 52 |  | 0 | 1
2053 | Active alarm group 53 |  | 0 | 1
2054 | Active alarm group 54 |  | 0 | 1
2055 | Active alarm group 55 |  | 0 | 1
2056 | Active alarm group 56 |  | 0 | 1
2057 | Active alarm group 57 |  | 0 | 1
2058 | Active alarm group 58 |  | 0 | 1
2059 | Active alarm group 59 |  | 0 | 1
2060 | Active alarm group 60 |  | 0 | 1
2061 | Active alarm group 61 |  | 0 | 1
2062 | Active alarm group 62 |  | 0 | 1
2063 | Active alarm group 63 |  | 0 | 1
2064 | Active alarm group 64 |  | 0 | 1
2065 | Active alarm group 65 |  | 0 | 1
2066 | Active alarm group 66 |  | 0 | 1
2067 | Active alarm group 67 |  | 0 | 1
2068 | Active alarm group 68 |  | 0 | 1
2069 | Active alarm group 69 |  | 0 | 1
2070 | Active alarm group 70 |  | 0 | 1
2071 | Active alarm group 71 |  | 0 | 1
2072 | Active alarm group 72 |  | 0 | 1
2073 | Active alarm group 73 |  | 0 | 1
2074 | Active alarm group 74 |  | 0 | 1
2075 | Active alarm group 75 |  | 0 | 1
2076 | Active alarm group 76 |  | 0 | 1
2077 | Active alarm group 77 |  | 0 | 1
2078 | Active alarm group 78 |  | 0 | 1
2079 | Active alarm group 79 |  | 0 | 1
2080 | Active alarm group 80 |  | 0 | 1
2081 | Active alarm group 81 |  | 0 | 1
2082 | Active alarm group 82 |  | 0 | 1
2083 | Active alarm group 83 |  | 0 | 1
2084 | Active alarm group 84 |  | 0 | 1
2085 | Active alarm group 85 |  | 0 | 1
2086 | Active alarm group 86 |  | 0 | 1
2087 | Active alarm group 87 |  | 0 | 1
2088 | Active alarm group 88 |  | 0 | 1
2089 | Active alarm group 89 |  | 0 | 1
2090 | Active alarm group 90 |  | 0 | 1
2091 | Active alarm group 91 |  | 0 | 1
2092 | Active alarm group 92 |  | 0 | 1
2093 | Active alarm group 93 |  | 0 | 1
2094 | Active alarm group 94 |  | 0 | 1
2095 | Active alarm group 95 |  | 0 | 1
2096 | Active alarm group 96 |  | 0 | 1
2097 | Active alarm group 97 |  | 0 | 1
2098 | Active alarm group 98 |  | 0 | 1
2099 | Active alarm group 99 |  | 0 | 1
2100 | Active alarm group 100 |  | 0 | 1

## Binary Output
GOLD_E_F_BACnet_230307
Binary Output (R/W).
Object Instance | Object Name | Description | Min | Max | Unit | Default | Misc
AHU fan regulation
1 | Booster diffusers | Booster diffusers function. | 0 | 1

## Binary Value
GOLD_E_F_BACnet_230307
Binary Value (R/W).
Object Instance | Object Name | Description | Min | Max | Unit | Default | Misc
Alarm settings
1 | Alarm reset | Resets all active alarms | 0 | 1 |  | 0
3 | Internal fire alarm function |  | 0 | 1 |  | 0
Pressure sensors zero point calibration
29 | SA flow pressure sensor auto zero calibration |  | 0 | 1 |  | 1
30 | EA flow pressure sensor auto zero calibration |  | 0 | 1 |  | 1
31 | SA duct pressure sensor auto zero calibration |  | 0 | 1 |  | 1
32 | EA duct pressure sensor auto zero calibration |  | 0 | 1 |  | 1
33 | ReCO2 pressure sensor auto zero calibration |  | 0 | 1 |  | 1
34 | RHX defrost pressure sensor auto calibration |  | 0 | 1 |  | 1
35 | Carry over control pressure sensor auto calibration |  | 0 | 1 |  | 1
36 | SA filter pressure sensor auto zero calibration |  | 0 | 1 |  | 1
37 | EA filter pressure sensor auto zero calibration |  | 0 | 1 |  | 1
38 | SA pre-filter pressure sensor auto zero calibration |  | 0 | 1 |  | 1
39 | EA pre-filter pressure sensor auto zero calibration |  | 0 | 1 |  | 1
40 | SA end-filter pressure sensor auto zero calibration |  | 0 | 1 |  | 1
41 | PX heat exchange pressure sensor auto calibration |  | 0 | 1 |  | 1 | 1.21
46 | SA flow pressure sensor activate zero calibration | If value is set to 1 for min 1s calibration will be performed. | 0 | 1 |  | 0
47 | EA flow pressure sensor activate zero calibration |  | 0 | 1 |  | 0
48 | SA duct pressure sensor activate zero calibration |  | 0 | 1 |  | 0
49 | EA duct pressure sensor activate zero calibration |  | 0 | 1 |  | 0
50 | ReCO2 pressure sensor activate calibration |  | 0 | 1 |  | 0
51 | RHX Defrost pressure sensor activate calibration |  | 0 | 1 |  | 0
52 | Carry over control pressure sensor activate zero calibration |  | 0 | 1 |  | 0
53 | SA filter pressure sensor activate zero calibration |  | 0 | 1 |  | 0
54 | EA filter pressure sensor activate zero calibration |  | 0 | 1 |  | 0
55 | SA pre-filter pressure sensor activate zero calibration |  | 0 | 1 |  | 0
56 | EA pre-filter pressure sensor activate zero calibration |  | 0 | 1 |  | 0
57 | SA end-filter pressure sensor activate zero calibration |  | 0 | 1 |  | 0
58 | PX heat exchange pressure sensor activate zero calibration |  | 0 | 1 |  | 0 | 1.21
AHU external sensors
162 | External room sensor 1 function |  | 0 | 1 |  | 0
163 | External room sensor 2 function |  | 0 | 1 |  | 0
164 | External room sensor 3 function |  | 0 | 1 |  | 0
165 | External room sensor 4 function |  | 0 | 1 |  | 0
167 | External room temp from BMS function |  | 0 | 1 |  | 0
172 | External OA sensor 1 function |  | 0 | 1 |  | 0
173 | External OA sensor 2 function |  | 0 | 1 |  | 0
174 | External OA sensor 3 function |  | 0 | 1 |  | 0
175 | External OA sensor 4 function |  | 0 | 1 |  | 0
177 | External OA temp from BMS function |  | 0 | 1 |  | 0
AHU Heat exchange
182 | RHX defrost function | Setting for activating the defrost function for the rotary heat exchanger. | 0 | 1 |  | 0
183 | RHX defrost calibration |  | 0 | 1 |  | 0
187 | RHX carry over control function | Setting for activating the carry over control function for the rotary heat exchanger. | 0 | 1 |  | 0
190 | RHX min exhaust air temp function |  | 0 | 1 |  | 0
198 | PHX periodic operation of bypass damper function |  | 0 | 1 |  | 1
201 | PX bypass optimize |  | 0 | 1 |  | 0 | 1.13
205 | CHX periodic operation of pump function |  | 0 | 1 |  | 1
206 | CHX periodic operation of valve function |  | 0 | 1 |  | 1
AHU Heat/Cool
228 | Re-heat periodic operation of pump function |  | 0 | 1 |  | 1
229 | Re-heat periodic operation of valve function |  | 0 | 1 |  | 1
245 | Extra regulation 1 periodic operation of pump function |  | 0 | 1 |  | 1
246 | Extra regulation 1 periodic operation of valve function |  | 0 | 1 |  | 1
274 | Cool relay 1 periodic operation of pump function |  | 0 | 1 |  | 0
275 | Cool relay 2 periodic operation of pump function |  | 0 | 1 |  | 0
276 | Cool periodic operation of valve function |  | 0 | 1 |  | 0
Summer night cool/Intermittent night heat /Morning boost
284 | Summer night cool function |  | 0 | 1 |  | 0
296 | Intermittent night heat function |  | 0 | 1 |  | 0
302 | Intermittent night heat recirculation function |  | 0 | 1 |  | 1 | 1.12
305 | Morning boost function |  | 0 | 1 |  | 0
Cooling boost/heating boost
320 | Heating boost function |  | 0 | 1 |  | 0
Xzone function
325 | Xzone heat function |  | 0 | 1 |  | 0
327 | Xzone cool function |  | 0 | 1 |  | 0
Xzone external sensors
374 | Xzone external room sensor 1 function |  | 0 | 1 |  | 0
375 | Xzone external room sensor 2 function |  | 0 | 1 |  | 0
376 | Xzone external room sensor 3 function |  | 0 | 1 |  | 0
377 | Xzone external room sensor 4 function |  | 0 | 1 |  | 0
379 | Xzone external room temp from BMS function |  | 0 | 1 |  | 0
Xzone Heat/Cool
386 | Xzone reheat periodic operation of pump function |  | 0 | 1 |  | 1
387 | Xzone reheat periodic operation of valve function |  | 0 | 1 |  | 1
400 | Xzone Cool relay 1 periodic operation of pump function |  | 0 | 1 |  | 0
401 | Xzone Cool relay 2 periodic operation of pump function |  | 0 | 1 |  | 0
402 | Xzone Cool periodic operation of valve function |  | 0 | 1 |  | 0
Pre-heat
410 | Pre-heat function |  | 0 | 1 |  | 0
414 | Pre-heat periodic operation of pump function |  | 0 | 1 |  | 1
415 | Pre-heat periodic operation of valve function |  | 0 | 1 |  | 1
ReCO2
425 | ReCO2 Calibration |  | 0 | 1 |  | 0
Humidity/VOC
457 | Dehumidifying function | Moved to Multistate Value 457 | 0 | 1 |  | 1 | 1.12
459 | Heat exchange active in dehumidifying sequence |  | 0 | 1 |  | 0
465 | VOC sensor function | Moved to Multistate Value 465 | 0 | 1 |  | 0 | 1.17
SMART Link
489 | SMART Link WB Cooling Optimize function |  | 0 | 1 |  | 0 | 1.26
490 | SMART Link WB Heating Optimize function |  | 0 | 1 |  | 0 | 1.26
504 | AQUA Link Function |  | 0 | 1 |  | 0
AYC
530 | AYC Heated water periodic operation of pump |  | 0 | 1 |  | 1
531 | AYC Heated water periodic operation of valve |  | 0 | 1 |  | 0
536 | AYC Heated water OA temp compensation |  | 0 | 1 |  | 0
547 | AYC Heated water room temp compensation function |  | 0 | 1 |  | 0
548 | AYC Heated water room temp compensation at night | 0=Enabled during night, 1=Disabled during night | 0 | 1 |  | 0
553 | AYC Heated water night temp compensation function |  | 0 | 1 |  | 0
579 | AYC Chilled water periodic operation of pump |  | 0 | 1 |  | 1
580 | AYC Chilled water periodic operation of valve |  | 0 | 1 |  | 0
585 | AYC Chilled water OA temp compensation |  | 0 | 1 |  | 0
596 | AYC Chilled water room temp compensation function |  | 0 | 1 |  | 0
597 | AYC Chilled water room temp compensation at night | 0=Enabled during night, 1=Disabled during night | 0 | 1 |  | 0
602 | AYC Chilled water night temp compensation function |  | 0 | 1 |  | 0
618 | AYC Chilled water dew point compensation air flow boost |  | 0 | 1 |  | 0
Optimize
637 | Optimize function |  | 0 | 1 |  | 0
Night temp compensation
775 | Night temp compensation function |  | 0 | 1 |  | 0 | 1.31
Reserved
824 | Extra regulation 2 periodic operation of pump function |  | 0 | 1 |  | 1 | 1.13
825 | Extra regulation 2 periodic operation of valve function |  | 0 | 1 |  | 1 | 1.13
BMS I/O-modules
1000 | External operation I/O-module A, function |  | 0 | 1 |  | 0 | 1.20
1001 | External operation I/O-module A, temp sensor 1 function |  | 0 | 1 |  | 0 | 1.20
1002 | External operation I/O-module A, temp sensor 2 function |  | 0 | 1 |  | 0 | 1.20
1003 | External operation I/O-module A, digital output |  | 0 | 1 |  | 0 | 1.20
1004 | External operation I/O-module B, function |  | 0 | 1 |  | 0 | 1.20
1005 | External operation I/O-module B, temp sensor 1 function |  | 0 | 1 |  | 0 | 1.20
1006 | External operation I/O-module B, temp sensor 2 function |  | 0 | 1 |  | 0 | 1.20
1007 | External operation I/O-module B, digital output |  | 0 | 1 |  | 0 | 1.20
1008 | External operation I/O-module C, function |  | 0 | 1 |  | 0 | 1.20
1009 | External operation I/O-module C, temp sensor 1 function |  | 0 | 1 |  | 0 | 1.20
1010 | External operation I/O-module C, temp sensor 2 function |  | 0 | 1 |  | 0 | 1.20
1011 | External operation I/O-module C, digital output |  | 0 | 1 |  | 0 | 1.20
External override
3000 | External override function, on/off |  | 0 | 1 |  | 0 | 1.30
3010 | External override value, Supply air fan, on/off |  | 0 | 1 |  | 0 | 1.30
3011 | External override value, Extract air fan, on/off |  | 0 | 1 |  | 0 | 1.30
3050 | External override value, Pre-heat relay, on/off |  | 0 | 1 |  | 0 | 1.30
3060 | External override value, Reheat relay, on/off |  | 0 | 1 |  | 0 | 1.30
3070 | External override value, Xzone heat relay, on/off |  | 0 | 1 |  | 0 | 1.30
3080 | External override value, Extra reg. 1 relay 1, on/off |  | 0 | 1 |  | 0 | 1.30
3081 | External override value, Extra reg. 1 relay 2, on/off |  | 0 | 1 |  | 0 | 1.30
3090 | External override value, Extra reg. 2 relay 1, on/off |  | 0 | 1 |  | 0 | 1.30
3091 | External override value, Extra reg. 2 relay 2, on/off |  | 0 | 1 |  | 0 | 1.30
3100 | External override value, Cool relay 1, on/off |  | 0 | 1 |  | 0 | 1.30
3101 | External override value, Cool relay 2, on/off |  | 0 | 1 |  | 0 | 1.30
3110 | External override value, Xzone cool relay 1, on/off |  | 0 | 1 |  | 0 | 1.30
3111 | External override value, Xzone cool relay 2, on/off |  | 0 | 1 |  | 0 | 1.30
3120 | External override value, COOL DX comp. 1 on/off |  | 0 | 1 |  | 0 | 1.30
3121 | External override value, COOL DX comp. 2 on/off |  | 0 | 1 |  | 0 | 1.30
3130 | External override value, HC, on/off |  | 0 | 1 |  | 0 | 1.30
3131 | External override value, HC cool/heat, on/off |  | 0 | 1 |  | 0 | 1.30
3132 | External override value, HC defrost, on/off |  | 0 | 1 |  | 0 | 1.30
3140 | External override value, SMART Link WB, on/off |  | 0 | 1 |  | 0 | 1.30
3141 | External override value, SMART Link WB, SMART Link WB cool/heat, on/off |  | 0 | 1 |  | 0 | 1.30
3150 | External override value, SMART Link DX 1, on/off |  | 0 | 1 |  | 0 | 1.30
3151 | External override value, SMART Link DX 1 cool/heat, on/off |  | 0 | 1 |  | 0 | 1.30
3152 | External override value, SMART Link DX 2, on/off |  | 0 | 1 |  | 0 | 1.30
3153 | External override value, SMART Link DX 2 cool/heat, on/off |  | 0 | 1 |  | 0 | 1.30
3154 | External override value, SMART Link DX 3, on/off |  | 0 | 1 |  | 0 | 1.30
3155 | External override value, SMART Link DX 3 cool/heat, on/off |  | 0 | 1 |  | 0 | 1.30
3156 | External override value, SMART Link DX 4, on/off |  | 0 | 1 |  | 0 | 1.30
3157 | External override value, SMART Link DX 4 cool/heat, on/off |  | 0 | 1 |  | 0 | 1.30
3160 | External override value, AQUA Link pump, on/off |  | 0 | 1 |  | 0 | 1.30
3170 | External override value, Humidifying relay, on/off |  | 0 | 1 |  | 0 | 1.30
3190 | External override value, AYC heat pump, on/off |  | 0 | 1 |  | 0 | 1.30
3191 | External override value, AYC cool pump, on/off |  | 0 | 1 |  | 0 | 1.30
3200 | External override value, AHU damper relay, on/off |  | 0 | 1 |  | 0 | 1.30
3201 | External override value, AHU operation relay, on/off |  | 0 | 1 |  | 0 | 1.30
3210 | External override value, Booster heat relay, on/off |  | 0 | 1 |  | 0 | 1.30
3211 | External override value, Booster cool relay, on/off |  | 0 | 1 |  | 0 | 1.30
3220 | External override value, Miru 1 fan, on/off |  | 0 | 1 |  | 0 | 1.30
3221 | External override value, Miru 2 fan, on/off |  | 0 | 1 |  | 0 | 1.30
3222 | External override value, Miru 3 fan, on/off |  | 0 | 1 |  | 0 | 1.30
4010 | External override activate, Supply air fan, on/off |  | 0 | 1 |  | 0 | 1.30
4011 | External override activate, Extract air fan, on/off |  | 0 | 1 |  | 0 | 1.30
4050 | External override activate, Pre-heat relay, on/off |  | 0 | 1 |  | 0 | 1.30
4060 | External override activate, Reheat relay, on/off |  | 0 | 1 |  | 0 | 1.30
4070 | External override activate, Xzone heat relay, on/off |  | 0 | 1 |  | 0 | 1.30
4080 | External override activate, Extra reg. 1 relay 1, on/off |  | 0 | 1 |  | 0 | 1.30
4081 | External override activate, Extra reg. 1 relay 2, on/off |  | 0 | 1 |  | 0 | 1.30
4090 | External override activate, Extra reg. 2 relay 1, on/off |  | 0 | 1 |  | 0 | 1.30
4091 | External override activate, Extra reg. 2 relay 2, on/off |  | 0 | 1 |  | 0 | 1.30
4100 | External override activate, Cool relay 1, on/off |  | 0 | 1 |  | 0 | 1.30
4101 | External override activate, Cool relay 2, on/off |  | 0 | 1 |  | 0 | 1.30
4110 | External override activate, Xzone cool relay 1, on/off |  | 0 | 1 |  | 0 | 1.30
4111 | External override activate, Xzone cool relay 2, on/off |  | 0 | 1 |  | 0 | 1.30
4120 | External override activate, COOL DX comp. 1 on/off |  | 0 | 1 |  | 0 | 1.30
4121 | External override activate, COOL DX comp. 2 on/off |  | 0 | 1 |  | 0 | 1.30
4130 | External override activate, HC, on/off |  | 0 | 1 |  | 0 | 1.30
4131 | External override activate, HC cool/heat, on/off |  | 0 | 1 |  | 0 | 1.30
4132 | External override activate, HC defrost, on/off |  | 0 | 1 |  | 0 | 1.30
4140 | External override activate, SMART Link WB, on/off |  | 0 | 1 |  | 0 | 1.30
4141 | External override activate, SMART Link WB, SMART Link WB cool/heat, on/off |  | 0 | 1 |  | 0 | 1.30
4150 | External override activate, SMART Link DX 1, on/off |  | 0 | 1 |  | 0 | 1.30
4151 | External override activate, SMART Link DX 1 cool/heat, on/off |  | 0 | 1 |  | 0 | 1.30
4152 | External override activate, SMART Link DX 2, on/off |  | 0 | 1 |  | 0 | 1.30
4153 | External override activate, SMART Link DX 2 cool/heat, on/off |  | 0 | 1 |  | 0 | 1.30
4154 | External override activate, SMART Link DX 3, on/off |  | 0 | 1 |  | 0 | 1.30
4155 | External override activate, SMART Link DX 3 cool/heat, on/off |  | 0 | 1 |  | 0 | 1.30
4156 | External override activate, SMART Link DX 4, on/off |  | 0 | 1 |  | 0 | 1.30
4157 | External override activate, SMART Link DX 4 cool/heat, on/off |  | 0 | 1 |  | 0 | 1.30
4160 | External override activate, AQUA Link pump, on/off |  | 0 | 1 |  | 0 | 1.30
4170 | External override activate, Humidifying relay, on/off |  | 0 | 1 |  | 0 | 1.30
4190 | External override activate, AYC heat pump, on/off |  | 0 | 1 |  | 0 | 1.30
4191 | External override activate, AYC cool pump, on/off |  | 0 | 1 |  | 0 | 1.30
4200 | External override activate, AHU damper relay, on/off |  | 0 | 1 |  | 0 | 1.30
4201 | External override activate, AHU operation relay, on/off |  | 0 | 1 |  | 0 | 1.30
4210 | External override activate, Booster heat relay, on/off |  | 0 | 1 |  | 0 | 1.30
4211 | External override activate, Booster cool relay, on/off |  | 0 | 1 |  | 0 | 1.30
4220 | External override activate, Miru 1 fan, on/off |  | 0 | 1 |  | 0 | 1.30
4221 | External override activate, Miru 2 fan, on/off |  | 0 | 1 |  | 0 | 1.30
4222 | External override activate, Miru 3 fan, on/off |  | 0 | 1 |  | 0 | 1.30
5010 | External override activate, Supply air fan level |  | 0 | 1 |  | 0 | 1.30
5011 | External override activate, Extract air fan level |  | 0 | 1 |  | 0 | 1.30
5020 | External override activate, RX HX level |  | 0 | 1 |  | 0 | 1.30
5030 | External override activate, PX HX damper 3A |  | 0 | 1 |  | 0 | 1.30
5031 | External override activate, PX HX damper 1A |  | 0 | 1 |  | 0 | 1.30
5032 | External override activate, PX HX bypass 2A |  | 0 | 1 |  | 0 | 1.30
5040 | External override activate, CX HX valve |  | 0 | 1 |  | 0 | 1.30
5041 | External override activate, CX HX pump level |  | 0 | 1 |  | 0 | 1.30
5050 | External override activate, Pre-heat level |  | 0 | 1 |  | 0 | 1.30
5060 | External override activate, Reheat level |  | 0 | 1 |  | 0 | 1.30
5070 | External override activate, Xzone heat level |  | 0 | 1 |  | 0 | 1.30
5080 | External override activate, Extra reg. 1 level |  | 0 | 1 |  | 0 | 1.30
5090 | External override activate, Extra reg. 2 level |  | 0 | 1 |  | 0 | 1.30
5100 | External override activate, Cool level |  | 0 | 1 |  | 0 | 1.30
5110 | External override activate, Xzone cool level |  | 0 | 1 |  | 0 | 1.30
5130 | External override activate, HC comp. level |  | 0 | 1 |  | 0 | 1.30
5131 | External override activate, HC defrost recirc. level |  | 0 | 1 |  | 0 | 1.30
5132 | External override activate, HC defrost el. heat level |  | 0 | 1 |  | 0 | 1.30
5150 | External override activate, SMART Link DX 1 comp. level |  | 0 | 1 |  | 0 | 1.30
5151 | External override activate, SMART Link DX 2 comp. level |  | 0 | 1 |  | 0 | 1.30
5152 | External override activate, SMART Link DX 3 comp. level |  | 0 | 1 |  | 0 | 1.30
5153 | External override activate, SMART Link DX 4 comp. level |  | 0 | 1 |  | 0 | 1.30
5170 | External override activate, Humidifying level |  | 0 | 1 |  | 0 | 1.30
5180 | External override activate, ReCO2 recirculation damper |  | 0 | 1 |  | 0 | 1.30
5181 | External override activate, ReCO2 outdoor damper |  | 0 | 1 |  | 0 | 1.30
5190 | External override activate, AYC heat valve level |  | 0 | 1 |  | 0 | 1.30
5191 | External override activate, AYC cool valve level |  | 0 | 1 |  | 0 | 1.30
5220 | External override activate, Miru 1 fan level |  | 0 | 1 |  | 0 | 1.30
5221 | External override activate, Miru 2 fan level |  | 0 | 1 |  | 0 | 1.30
5222 | External override activate, Miru 3 fan level |  | 0 | 1 |  | 0 | 1.30

## Calendar
GOLD_E_F_BACnet_230307
Calendar
Object Instance | Object Name | Description | Min | Max | Unit | Default | Misc
0 | Calendar #1 | DateList: max. 10 entries with dates from 1.1.2000 to 31.12.2099.
1 | Calendar #2 | DateList: max. 10 entries with dates from 1.1.2000 to 31.12.2099.

## Multistate Input
GOLD_E_F_BACnet_230307
Multistate Input (RO).
Object Instance | Object Name | Description | Min | Max | Unit | Default | Misc
AHU Air flow/duct pressure
2 | Application id/AHU Type | State text. 1=GOLD RX 2=GOLD PX 3=GOLD CX 4=GOLD SD/SA 5=GOLD SD/EA 6=GOLD SD/SA+CX 7=GOLD SD/SA+EA 8=GOLD SD/SA+EA+CX | 1 | 8
3 | Air flow direction | State text. 1=Fan no.2 as SA 2=Fan no.1 as SA | 1 | 2
AHU heat exchange
114 | PHX-2 3D Type | State text. 1=Cross flow 2=Counter flow | 1 | 2 |  |  | 1.21
115 | PHX type | State text. 1=PHX-1 1D HS (one damper and humidity sensor) 2=PHX-2 3D (three dampers) 3=PHX-3 1D 1PS (one damper and pressure sensor) | 1 | 3 |  |  | 1.16
AHU Coils
140 | Extra regulation sequence 1 coil type | State text. 1=None 2=1 Electric 3=2 Electric 4=3 Electric 5=4 Electric 6=5 Electric 7=6 Electric 8=7 Electric 9=8 Electric 10=9 Water 11=10 Water 12=11 Electric 13=12 Electric 14=13 Electric 15=14 Electric 16=15 Electric | 1 | 16
142 | Extra regulation sequence 2 coil type | State text. 1=None 2=1 Electric 3=2 Electric 4=3 Electric 5=4 Electric 6=5 Electric 7=6 Electric 8=7 Electric 9=8 Electric 10=9 Water 11=10 Water 12=11 Electric 13=12 Electric 14=13 Electric 15=14 Electric 16=15 Electric | 1 | 16 |  |  | 1.13
152 | Re-heat coil type | State text. 1=None 2=1 Electric 3=2 Electric 4=3 Electric 5=4 Electric 6=5 Electric 7=6 Electric 8=7 Electric 9=8 Electric 10=9 Water 11=10 Water 12=11 Electric 13=12 Electric 14=13 Electric 15=14 Electric 16=15 Electric | 1 | 16
163 | Cool coil type | State text. 1=None 2=1 Electric 3=2 Electric 4=3 Electric 5=4 Electric 6=5 Electric 7=6 Electric 8=7 Electric 9=8 Electric 10=9 Water 11=10 Water 12=11 Electric 13=12 Electric 14=13 Electric 15=14 Electric 16=15 Electric | 1 | 16
Xzone coils
198 | Xzone heat, coil type | State text. 1=None 2=1 Electric 3=2 Electric 4=3 Electric 5=4 Electric 6=5 Electric 7=6 Electric 8=7 Electric 9=8 Electric 10=9 Water 11=10 Water 12=11 Electric 13=12 Electric 14=13 Electric 15=14 Electric 16=15 Electric | 1 | 16
209 | Xzone cool, coil type | State text. 1=None 2=1 Not used 3=2 Not used 4=3 Not used 5=4 Not used 6=5 Not used 7=6 Not used 8=7 Not used 9=8 Not used 10=9 Water 11=10 Water 12=11 Not used 13=12 Not used 14=13 Not used 15=14 Not used 16=15 Not used | 1 | 16
Pre-heat
224 | Pre-heat coil type | State text. 1=None 2=1 Electric 3=2 Electric 4=3 Electric 5=4 Electric 6=5 Electric 7=6 Electric 8=7 Electric 9=8 Electric 10=9 Water 11=10 Water 12=11 Electric 13=12 Electric 14=13 Electric 15=14 Electric 16=15 Electric | 1 | 16
SMART Link
320 | SMART Link, DX cool mode | State text. 1=Heat 2=Cool | 1 | 2
Operation level
592 | Operation level | State text. 1=Fan not available 2=Alarm stop 3=Manual total stop (on hand terminal) 4=External total stop (digital input) 5=Communication total stop 6=Communication normal stop 7=Communication extended normal stop 8=Time channel total stop 9=Time channel normal stop 10=Time channel extended normal stop 11=Low speed=normal stop 12=SA Fan starting up 13=Fan regulation blocked 14=ReCO2 100% recirculation(1.11) 15=Morning boost stop(1.11) 16=Intermittent night heat stop(1.11) 17=After cooling electric heater 18=COOL DX switch off delay 19=Damper switch off delay 20=Manual low speed (on hand terminal) 21=External low speed (digital input) 22=Extended external low speed 23=Communication low speed 24=Time channel low speed 25=Morning boost low speed 26=Intermittent night heat low speed 27=Manual high speed (on hand terminal) 28=External high speed (digital input) 29=Extended external high speed 30=Communication high speed 31=Time channel high speed 32=Summer night cooling high speed 33=Filter calibration 34=RHX Defrost calibration 35=ReCO2 calibration 36=AHU start up 37=Re-heat ramp down 38=HX ramp down 39=Air adjustment 40=Fans in operation with active fire alarm 41=PX bypass damper adjustment(1.12) | 1 | 41 |  |  | 1.12 | ,
H/C
665 | Schedule exception invalid data | State text. 1=Inactive 2=Active | 1 | 2 |  |  | 2.34
666 | Calendar 1 invalid data | State text. 1=Inactive 2=Active | 1 | 2 |  |  | 2.34
667 | Calendar 2 invalid data | State text. 1=Inactive 2=Active | 1 | 2 |  |  | 2.34
H/C
1400 | H/C mode | State text. 1=Inactive 2=Active | 1 | 2 |  |  | 1.23
1401 | H/C defrost accessory | State text. 1=Inactive 2=Recirculation 3=Electric heat | 1 | 3 |  |  | 1.23
1402 | H/C recirculation defrost active | State text. 1=Inactive 2=Active | 1 | 2 |  |  | 1.31
1403 | H/C defrost active | State text. 1=Inactive 2=Active | 1 | 2 |  |  | 1.31
1407 | H/C heat type | State text. 1=None 2=1 Electric 3=2 Electric 4=3 Electric 5=4 Electric 6=5 Electric 7=6 Electric 8=7 Electric 9=8 Electric 10=9 Water 11=10 Water 12=11 Electric 13=12 Electric 14=13 Electric 15=14 Electric 16=15 Electric | 1 | 16 |  |  | 1.23
1410 | H/C operation mode | State text. 1=Inactive 2=Stop 3=Stabilization 4=Normal operation 5=Comfort operation 6=Economy operation 7=Defrost 8=Defrost 9=Oil recovery | 1 | 9 |  |  | 1.23
1411 | H/C defrost mode | State text. 1=Inactive 2=Start delay 3=Initializing 4=Pre-defrosting 5=Defrosting 6=Draining | 1 | 6 |  |  | 1.23
1412 | H/C heat/cool mode | State text. 1=Heating 2=Cooling | 1 | 2 |  |  | 1.23

## Multistate Output
GOLD_E_F_BACnet_230307
Multistate Output (R/W).
Object Instance | Object Name | Description | Min | Max | Unit | Default | Misc
AHU fan regulation
1 | Boost Supply air | State text. 1=Off 2=On | 1 | 2 |  | 1
2 | Boost Extract air | State text. 1=Off 2=On | 1 | 2 |  | 1

## Multistate Value
GOLD_E_F_BACnet_230307
Multistate Value (R/W).
Object Instance | Object Name | Description | Min | Max | Unit | Default | Misc
AHU fan regulation
1 | SA Fan regulation mode | Setting of regulation type for the supply air fan. State text. 1=Air flow reg. 2=Pressure reg. 3=Demand reg. 4=Slave controlled by EA fan | 1 | 4 |  | 1
2 | EA Fan regulation mode | Setting of regulation type for the extract air fan. State text. 1=Air flow reg. 2=Pressure reg. 3=Demand reg. 4=Slave controlled by SA fan | 1 | 4 |  | 1
Alarm settings
4 | Internal fire alarm reset function | State text. 1=Manual reset 2=Auto reset | 1 | 2 |  | 1
7 | External fire alarm no. 1 reset function | State text. 1=Manual reset 2=Auto reset | 1 | 2 |  | 1
8 | External fire alarm no. 2 reset function | State text. 1=Manual reset 2=Auto reset | 1 | 2 |  | 1
11 | External alarm no. 1 reset function | State text. 1=Manual reset 2=Auto reset | 1 | 2 |  | 1
12 | External alarm no. 2 reset function | State text. 1=Manual reset 2=Auto reset | 1 | 2 |  | 1
15 | External alarm no. 1 input function | State text. 1=Alarm at closed contact 2=Alarm at open contact | 1 | 2 |  | 1
16 | External alarm no. 2 input function | State text. 1=Alarm at closed contact 2=Alarm at open contact | 1 | 2 |  | 1
Fans OA temp compensation
53 | Outdoor temp compensation function | State text. 1=Inactive 2=Active at low speed 3=Active at high speed 4=Active at low and high speed | 1 | 4 |  | 1
Fans down regulation
78 | Down regulation function | State text. 1=Inactive 2=SA 3=SA and EA | 1 | 3 |  | 2
Fans in operation at active fire alarm
84 | Fans in operation at fire alarm 1 function | State text. 1=Inactive 2=SA 3=EA 4=SA and EA | 1 | 4 |  | 1
87 | Fans in operation at fire alarm 2 function | State text. 1=Inactive 2=SA 3=EA 4=SA and EA | 1 | 4 |  | 1
90 | Fans in operation at internal fire alarm function | State text. 1=Inactive 2=SA 3=EA 4=SA and EA | 1 | 4 |  | 1
Filters
95 | Pre-filter function | State text. 1=Inactive 2=SA 3=EA 4=SA and EA | 1 | 4 |  | 1
96 | Pre-filter calibration | State text. 1=Inactive 2=SA 3=EA 4=SA and EA | 1 | 4 |  | 1
101 | AHU filter function | State text. 1=Inactive 2=SA 3=EA 4=SA and EA | 1 | 4
102 | AHU filter calibration | State text. 1=Inactive 2=SA 3=EA 4=SA and EA | 1 | 4 |  | 1
107 | SA end filter function | State text. 1=Inactive 2=SA | 1 | 2
108 | SA end filter calibration | State text. 1=Inactive 2=SA | 1 | 2 |  | 1
AHU Temperature regulation
111 | Seasonal controlled temperature regulation | State text. 1=Inactive 2=Active | 1 | 2 |  | 1 | 1.23
112 | Seasonal controlled temperature regulation mode | State text. 1=ERS-1 2=ERS-2 3=SA 4=EA 5=ORS 6=ORE | 1 | 6 |  | 4 | 1.23
115 | Temperature regulation mode | State text. 1=Inactive 2=ERS-1 3=ERS-2 4=SA 5=EA 6=ORS 7=ORE | 1 | 7 |  | 4
AHU external sensors
166 | External room sensors measurement function | State text. 1=Average 2=Min 3=Max | 1 | 3 |  | 1
176 | External OA sensors measurement function | State text. 1=Average 2=Min 3=Max | 1 | 3 |  | 1
AHU Heat exchange
188 | RHX sorption rotor function | Setting for activating the sorption rotor control function for the rotary heat exchanger. State text. 1=Inactive 2=Sorption max at cool 3=Sorption always max | 1 | 3 |  | 1 | 1.16
189 | Rotor type | State text. 1=RECOnomic 2=STE 3=MPE 4=MTE | 1 | 4 |  | 1 | 2.36
AHU Heat/Cool
236 | Extra regulation 1 combi coil output indication | State text. 1=Heat 2=Cool | 1 | 2 |  | 1 | 2.37
237 | Extra regulation sequence 1 function | State text 1=Inactive 2=Heat 3=Cool 4=Heat and Cool | 1 | 4 |  | 1
238 | Extra regulation sequence 1 output function | State text. 1=0-10V 2=10-0V | 1 | 2 |  | 1
249 | Extra regulation 1 combi coil external signal indication | State text. 1=Heat 2=Cool | 1 | 2 |  | 1 | 1.26
250 | Extra regulation 1 combi coil external signal value | State text. 1=Inactive 2=Active | 1 | 2 |  | 1 | 1.26
251 | Extra regulation 1 temperature protection function | State text. 1=Inactive 2=Active | 1 | 2 |  | 1
254 | Season heat function | State text. 1=Inactive 2=Extra regulation sequence at closed input 3=Extra regulation sequence at open input 4=Manual mode | 1 | 4 |  | 1
255 | Season heat manual setting | State text. 1=Re-heat 2=Extra regulation sequence | 1 | 2 |  | 1
261 | Cool on/off regulation function | State text. 1=Inactive 2=1 step 3=2 steps 4=3 steps | 1 | 4 |  | 1
Cooling boost/heating boost
313 | Cooling boost function | State text. 1=Inactive 2=Comfort 3=Economy 4=Sequence 5=Comfort and Economy 6=Economy and Sequence 7=Sequence and Comfort 8=Comfort, Economy and Sequence | 1 | 6 |  | 1 | 1.20
Xzone temperature regulation
329 | Xzone temperature regulation mode | State text. 1=Inactive 2=ERS-1 3=ERS-2 4=SA 5=EA 6=ORS 7=ORE | 1 | 7 |  | 1
Xzone external sensors
378 | Xzone external room sensors measurement function | State text. 1=Average 2=Min 3=Max | 1 | 3 |  | 1
Xzone Heat/Cool
395 | Xzone Cool on/off regulation function | State text. 1=Inactive 2=1 step 3=2 steps 4=3 steps | 1 | 4 |  | 1
ReCO2
423 | ReCO2-CO2 function | State text. 1=Inactive 2=CO2 3=CO2 and air flow boost | 1 | 3 |  | 1
424 | ReCO2 temperature regulation sequence function | State text. 1=Inactive 2=Heat 3=Cool 4=Heat and Cool | 1 | 4 |  | 1
Humidity/VOC
441 | Humidifying function | State text. 1=Inactive 2=On/Off 3=0-10V | 1 | 3 |  | 1
442 | Humidifying sensor | State text. 1=SA 2=EA | 1 | 2 |  | 1
457 | DeHumidifying function | State text. 1=Inactive 2=SA 3=EA | 1 | 3 |  | 1 | 1.12
465 | VOC sensor function | State text. 1=Inactive 2=Monitoring only 3=Monitoring and regulation | 1 | 3 |  | 1 | 1.17
COOL DX
469 | COOL DX Function | State text. 1=Inactive 2=Economy 3=Comfort 4=Top | 1 | 4 |  | 1
SMART Link
481 | SMART Link Function | State text. 1=Inactive 2=Water based heat pump 3=Water based chiller 4=Water based reversible 5=DX based heat pump 6=DX based chiller 7=DX based reversible | 1 | 7 |  | 1
505 | AQUA Link Pump alarm function | State text. 1=Inactive 2=Alarm at closed contact 3=Alarm at open contact 4=Alarm when in -and output are unequal (contactor function) | 1 | 4
AYC
521 | AYC Function | State text. 1=Inactive 2=Chilled water 3=Heated water 4=Chilled and heated water | 1 | 4 |  | 1
528 | AYC Heated water signal monitor function for pump | State text. 1=Inactive 2=Alarm at open contact 3=Alarm at closed contact 4=Contactor function | 1 | 4 |  | 1
555 | AYC Heated water night temp compensation time 1 (days) | State text. 1=Inactive 2=Monday 3=Tuesday 4=Wednesday 5=Thursday 6=Friday 7=Saturday 8=Sunday 9=Monday to Friday 10= Monday to Sunday 11=Saturday to Sunday | 1 | 11 |  | 1
562 | AYC Heated water night temp compensation time 2 (days) | State text. 1=Inactive 2=Monday 3=Tuesday 4=Wednesday 5=Thursday 6=Friday 7=Saturday 8=Sunday 9=Monday to Friday 10= Monday to Sunday 11=Saturday to Sunday | 1 | 11 |  | 1
577 | AYC Chilled water signal monitor function for pump | State text. 1=Inactive 2=Alarm at open contact 3=Alarm at closed contact 4=Contactor function | 1 | 4 |  | 1
604 | AYC Chilled water night temp compensation time 1 (days) | State text. 1=Inactive 2=Monday 3=Tuesday 4=Wednesday 5=Thursday 6=Friday 7=Saturday 8=Sunday 9=Monday to Friday 10= Monday to Sunday 11=Saturday to Sunday | 1 | 11 |  | 1
611 | AYC Chilled water night temp compensation time 2 (days) | State text. 1=Inactive 2=Monday 3=Tuesday 4=Wednesday 5=Thursday 6=Friday 7=Saturday 8=Sunday 9=Monday to Friday 10= Monday to Sunday 11=Saturday to Sunday | 1 | 11 |  | 1
MIRU Control
660 | MIRU Control 1 function | State text. 1=Inactive 2=Parallel start 3=Parallel low / high speed 4=Parallel start and Low / high speed | 1 | 4 |  | 1
661 | MIRU Control 2 function | State text. 1=Inactive 2=Parallel start 3=Parallel low / high speed 4=Parallel start and Low / high speed | 1 | 4 |  | 1
662 | MIRU Control 3 function | State text. 1=Inactive 2=Parallel start 3=Parallel low / high speed 4=Parallel start and Low / high speed | 1 | 4 |  | 1
663 | MIRU Control 4 function | State text. 1=Inactive 2=Parallel start 3=Parallel low / high speed 4=Parallel start and Low / high speed | 1 | 4 |  | 1
664 | MIRU Control 5 function | State text. 1=Inactive 2=Parallel start 3=Parallel low / high speed 4=Parallel start and Low / high speed | 1 | 4 |  | 1
665 | MIRU Control 6 function | State text. 1=Inactive 2=Parallel start 3=Parallel low / high speed 4=Parallel start and Low / high speed | 1 | 4 |  | 1
666 | MIRU Control 7 function | State text. 1=Inactive 2=Parallel start 3=Parallel low / high speed 4=Parallel start and Low / high speed | 1 | 4 |  | 1
667 | MIRU Control 8 function | State text. 1=Inactive 2=Parallel start 3=Parallel low / high speed 4=Parallel start and Low / high speed | 1 | 4 |  | 1
668 | MIRU Control 9 function | State text. 1=Inactive 2=Parallel start 3=Parallel low / high speed 4=Parallel start and Low / high speed | 1 | 4 |  | 1
669 | MIRU Control 10 function | State text. 1=Inactive 2=Parallel start 3=Parallel low / high speed 4=Parallel start and Low / high speed | 1 | 4 |  | 1
671 | MIRU Control 1 Balanced air flow function | State text. 1=Inactive 2=SA 3=EA | 1 | 3 |  | 1
679 | MIRU Control 2 Balanced air flow function | State text. 1=Inactive 2=SA 3=EA | 1 | 3 |  | 1
687 | MIRU Control 3 Balanced air flow function | State text. 1=Inactive 2=SA 3=EA | 1 | 3 |  | 1
695 | MIRU Control 4 Balanced air flow function | State text. 1=Inactive 2=SA 3=EA | 1 | 3 |  | 1
703 | MIRU Control 5 Balanced air flow function | State text. 1=Inactive 2=SA 3=EA | 1 | 3 |  | 1
711 | MIRU Control 6 Balanced air flow function | State text. 1=Inactive 2=SA 3=EA | 1 | 3 |  | 1
719 | MIRU Control 7 Balanced air flow function | State text. 1=Inactive 2=SA 3=EA | 1 | 3 |  | 1
727 | MIRU Control 8 Balanced air flow function | State text. 1=Inactive 2=SA 3=EA | 1 | 3 |  | 1
735 | MIRU Control 9 Balanced air flow function | State text. 1=Inactive 2=SA 3=EA | 1 | 3 |  | 1
743 | MIRU Control 10 Balanced air flow function | State text. 1=Inactive 2=SA 3=EA | 1 | 3 |  | 1
Neutral zone
765 | Heat neutral zone function | State text. 1=Set point 2=Start limit | 1 | 2 |  | 1 | 1.32
766 | Cool neutral zone function | State text. 1=Set point 2=Start limit | 1 | 2 |  | 1 | 1.32
Night temp compensation
777 | Night temp compensation time 1 (days) | State text. 1=Inactive 2=Monday 3=Tuesday 4=Wednesday 5=Thursday 6=Friday 7=Saturday 8=Sunday 9=Monday to Friday 10= Monday to Sunday 11=Saturday to Sunday | 1 | 11 |  | 1 | 1.31
782 | Night temp compensation time 2 (days) | State text. 1=Inactive 2=Monday 3=Tuesday 4=Wednesday 5=Thursday 6=Friday 7=Saturday 8=Sunday 9=Monday to Friday 10= Monday to Sunday 11=Saturday to Sunday | 1 | 11 |  | 1 | 1.31
Operation level settings
793 | Communication operation level | State text. 1=Auto 2=Total stop 3=Low speed 4=High speed 5=Normal stop 6=Extended normal stop | 1 | 6 |  | 1
794 | Schedule operation level | State text. 1=Total stop 2=Low speed 3=High speed 4=Normal stop 5=Extended normal stop | 1 | 5 |  |  | 1.23
Reserved
816 | Extra regulation sequence 2 function | State text. 1=Inactive 2=Heat 3=Cool 4=Heat and Cool | 1 | 4 |  | 1 | 1.13
817 | Extra regulation sequence 2 output function | State text. 1=0-10V 2=10-0V | 1 | 2 |  | 1 | 1.13
828 | Extra regulation 2 combi coil external signal indication | State text. 1=Heat 2=Cool | 1 | 2 |  | 1 | 1.26
829 | Extra regulation 2 combi coil external signal value | State text. 1=Inactive 2=Active | 1 | 2 |  | 1 | 1.26
834 | Extra regulation 2 combi coil output indication | State text. 1=Heat 2=Cool | 1 | 2 |  | 1 | 2.37
H/C
850 | H/C heat mode | State text. 1=Standard 2=Comfort | 1 | 2 |  | 1 | 1.23
851 | H/C cool mode | State text. 1=Standard 2=Comfort | 1 | 2 |  | 1 | 1.23
Humidifying
890 | Humidifying time 1 (days) | State text. 1=Inactive 2=Monday 3=Tuesday 4=Wednesday 5=Thursday 6=Friday 7=Saturday 8=Sunday 9=Monday to Friday 10= Monday to Sunday 11=Saturday to Sunday | 1 | 11 |  | 1 | 2.37
895 | Humidifying time 2 (days) | State text. 1=Inactive 2=Monday 3=Tuesday 4=Wednesday 5=Thursday 6=Friday 7=Saturday 8=Sunday 9=Monday to Friday 10= Monday to Sunday 11=Saturday to Sunday | 1 | 11 |  | 1 | 2.37
900 | Humidifying time 3 (days) | State text. 1=Inactive 2=Monday 3=Tuesday 4=Wednesday 5=Thursday 6=Friday 7=Saturday 8=Sunday 9=Monday to Friday 10= Monday to Sunday 11=Saturday to Sunday | 1 | 11 |  | 1 | 2.37
905 | Humidifying time 4 (days) | State text. 1=Inactive 2=Monday 3=Tuesday 4=Wednesday 5=Thursday 6=Friday 7=Saturday 8=Sunday 9=Monday to Friday 10= Monday to Sunday 11=Saturday to Sunday | 1 | 11 |  | 1 | 2.37

## Notification Class
GOLD_E_F_BACnet_230307
Notification Class
Object Instance | Object Name | Description | Min | Max | Unit | Default | Misc
0 | NC 00 A-Alarm | Notification Class 00 for AHU A-Alarm.
1 | NC 01 B-Alarm | Notification Class 01 for AHU B-Alarm.
3 | NC 03 Alarms specified in BACnet | Notification Class 03 for alarms specified in BACnet objects.
10 | NC 10 Info message | Notification Class 10 for AHU Info message.
11 | NC 11 Events specified in BACnet | Notification Class 11 for events specified in BACnet objects.

## Schedule
GOLD_E_F_BACnet_230307
Schedule
Object Instance | Object Name | Description | Min | Max | Unit | Default | Misc
0 | Schedule #1 | Weekly_Schedule: max. 6 Time-Values per day. Exception_Schedule: max. 2 entries with 6 Time-Values each. The value-range is a value(Unsigned) between 1-5, the time-range is from 00:00 to 23:59, where seconds and hundredths of seconds must be set to zero. 1=Total stop 2=Low speed 3=High speed 4=Normal stop 5=Extended normal stop 6=